## Comparison
NOTE: This table was created using the yellow user input expectation of 0% degradation. Just beware of changing it.
Summary statistics for U.S. PV system fleet samples |  |  |  | Supplementary statistics for U.S. PV system fleet samples
Unweighted for size. Expected PR: 0.8 fixed, 0.76 trkr
Set A: 100 longest-running systems (typical full operation begins 2011)
Set B: 25 systems (typical full operation begins 2019)
| Set A | Set B | Finding |  | Set A | Set B | Finding
Median lifetime, years | 14 | 6 | Set B was chosen to compare against first 7 years of Set A. | Median 7-yr production variability, ±% | 5.054% | 6.236% | Newer set shows higher variability
Median PI, first 7 years | 0.93178 | 0.88714 | Newer systems are performing a bit worse than the oldies!? | Inter-annual POA variability, ±% | 3% | 3.2% | and a smaller percentage that can
Std deviation of 7-yr PI | 0.11458 | 0.13007 | Newer set has a higher std dev, but 1/4th the sample size. | % "explainable" production variability | 59.49% | 51.57% | be explained by weather
Median PI, overall lifetime | 0.87759 | 0.88714 | However, shouldn't compare PI over vastly different lifetimes. | Median lifetime production variability, ±% | 10.42% | same as
Std deviation of lifetime PI | 0.14359 | 0.13007 | For Set B, the lifetime std dev is of course the same as for 7 yrs. | Inter-annual POA variability, ±% | 3% | 7-yr
|  |  |  | % "explainable" production variability | 28.96% | above
Degr, first 7 yrs | -0.6966% | -0.4446% | Newer PV is either more stable or some degr is hidden by clipping.
Degr, beyond 7 yrs | -4.201% | n/a | Beyond 7 years, performance is nosediving among older systems.
Median MWp | 2.2 | 2.7 | Newer systems are only moderately larger.
Median ILR | 1.125 | 1.3333 | Newer systems have much higher ILRs.
Median daily POA | 5.6726 | 5.1712 | Newer systems include many cloudier places.
Median DF | 0.36579 | 0.44733 | Yes, newer systems are definitely going into much cloudier places.
Typical clip% | 0.01484% | 2.293% | Based on Townsend's CCC work, clip =f(POA,ILR,DF).
Hidden clipping portion | 0.1927% | 25.77% | Based on Townsend PVsyst modeling w/1% dc degr.
% tracking systems | 34% | 32% | Surprisingly, a slight dip in tracker popularity?
% hot locations (Tmod>50) | 12% | 4% | And a notable shift away from hot locations, moving to
% cold locations (Tmod<40) | 47% | 72% | colder locations.
7-yr PI in hot locations | 0.85869 | 0.89112 | In Set A's 100 cases, the PI is markedly worse in hot locations.
7-yr PI in cold locations | 0.93789 | 0.9032 | In Set B's 25 cases, the comparison is meaningless, since there
was only 1 hot location out of the 25 I randomly selected.
16-yr degr in hot locations | -5.566% | n/a | In Set A's 100 cases, the degr is markedly worse in hot locations.
16-yr degr in cold locations | -1.719% | n/a | In Set B's 25 cases, a degr comparison isn't meaningful.

## PlantData
Annual output for the EIA's 100 oldest PV systems. Some older systems were excluded; their size kept changing (Springerville, Prescott), or they are solar thermal (SEGS), or mislabeled as solar (Saguaro), or just stunk (a few operated sporadically for 1-5 yrs, then vanished) | [34 empty] | Top 12 states w/more than 1% (8 more states had 1 system apiece) | [9 empty] | Tracker | Fixed |  |  | 0.93076 | 0.9358 | 0.97256 | 1.0755 | PI, by year, with user's degradation allowance included as a user input variable (try 0% degr to see a fanning cloud of degrading outputs) | [14 empty] | ann. p50 SLD degr, yr1-7> | -0.6966% | -0.0066091 | 0.97518 |  | p50 SLD degr, yr7-16> | -4.201% | -0.035077 | 0.99278 |  | min PI | 0.34363 | avg PI | 0.84068 |  | -2.57% | -0.022321 | 1.0472 | SLD degr rate over 16 yrs for the median system | [38 empty] | Full lifetime | Full lifetime | Full lifetime | Full lifetime | [32 empty] | 5.1%
data w/eqn. | just data | < data entry color key | [10 empty] | MWp | 639.9495 |  | Top100 calcs, wtd by energy |  | 42.9787 | <POA-wtd Tmod |  |  |  | avg> | 1.683% | 84.84% |  | w/o degr | w/degr | MWh-wtd PI |  | smallest | 0.2576 | MWp |  | CA | 30% | NC | 7% | FL | 4% | MA | 3% |  |  | %,PI,MWp | %,PI,MWp |  |  |  | ann. p90 expon degr, Yr1-Yr16 > | -6.924% | p90 (statistical) | 0.75243 | 0.69588 | 0.67727 | 0.69566 | 0.67347 | 0.67136 | 0.69748 | 0.57178 | 0.49316 | 0.50433 | 0.54204 | 0.48218 | 0.43292 | 0.22628 | 0.24115 | 0.29282 | 0.29356 | [8 empty] | median PI | 0.87759 | p90(1.28σ) | 0.65689 |  | -6.099% | -0.035747 | 0.87209 | SLD degr rate over 16 yrs for the p90 system | [38 empty] | # of systems | # of systems | # of systems | # of systems | 7-yr only | 7-yr only | [29 empty] | Median | Median | Median | Median | Median
| Expected PR | Fixed | 0.8 |  | Fleet median degradation, 1st 7 yrs |  | -0.6966% |  | Expctd Degr | 0.5% |  |  | MW,ac | 543.706 |  | 13660673.45 | MWh,act. | 42.0172 | < median Tmod |  |  |  | median> | 0.01484% | 99.81% |  | 13660673.45 |  | 88.21% |  | average | 6.3995 | MWp |  | NJ | 16% | PA | 6% | NM | 4% | HI | 2% |  |  | 34% | 66% | [5 empty] | avg | 0.9275 | 0.92705 | 0.91518 | 0.91692 | 0.89989 | 0.89725 | 0.88502 | 0.84883 | 0.79713 | 0.80256 | 0.81054 | 0.78545 | 0.74837 | 0.64249 | 0.59641 | 0.58775 | 0.69958 | 0 | 0 | 0 | 0 | 0.040784 | 0.1542 |  |  | max PI | 1.055 | p90(rank) | 0.65411 | -2.33% | [21 empty] | 1 | Most common |  | # at mode | 68 | [14 empty] | Median 7-yr PI | 0.93178 | 12 | 12 | 47 | 47 | 12 | 47 |  |  | median | [26 empty] | 10.42% | 3% | 28.96% | 5.054% | 59.49%
| (user input) | Tracker | 0.76 |  | Fleet median degradation, last 9 yrs |  | -4.201% |  | MedianPI> | 0.87759 | (unwghtd) |  | ILR | 1.177 |  | 14987169.1151 | MWh,exp. | eqn uses PVsyst | T,mod zones |  |  |  |  | CCC-based | estim. |  | 15486387.4082 | 14987169.1151 | 91.15% |  | largest | 60.5 | MWp |  | CO | 8% | AZ | 6% | NV | 4% | TX | 2% |  |  | 0.82252 | 0.85004 |  |  |  | ann. p50 expon degr, Yr1-Yr16 > | -2.744% | Median | 0.95385 | 0.97112 | 0.96056 | 0.95053 | 0.95069 | 0.93482 | 0.91966 | 0.91175 | 0.87512 | 0.84431 | 0.8688 | 0.83999 | 0.7788 | 0.73854 | 0.60729 | 0.6143 | 0.76679 | 0 | 0 | 0 | 0 | 0.040784 | 0.1542 |  | Lifetime expected energy over number of years reported in the EIA database | [13 empty] | Temp. Zone (>50,>40,<40) |  |  |  | System Size Differentiator |  |  |  | Ownership Differentiator |  |  |  |  | Delay Differentiator: years between start-up & full ops |  |  |  |  | Developer Differentiator |  |  |  |  | Module type differentiator | [8 empty] | Std dev of 7-yr PI | 0.11458 | Median PI | Median Degr | Median PI | Median Degr | Median PI | Median PI |  |  | -1.114% |  |  | -3.046% | Inter-annual variability (IAV) analysis of generation and insolation (to the right) | [23 empty] | orientation
|  |  | 2011 | 34 | [8 empty] | 2.2 |  | 2071.9342 | 91.15% | < Fleet PI, wtd. | at 10 cities | H>50, M>40, |  |  |  | 0.36579 | Corr'n. | Visible |  | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right | [17 empty] | 6.7109 | 6.2391 |  |  |  | Median age |  | stdev | 0.13677 | 0.1806 | 0.18586 | 0.17286 | 0.17689 | 0.17647 | 0.14652 | 0.21645 | 0.23748 | 0.23299 | 0.20977 | 0.23693 | 0.24645 | 0.32516 | 0.27754 | 0.23041 | 0.31721 | [7 empty] | This term uses the economics formula F/A, uniform series compound amount factor | [8 empty] | Average PI and degradation by state |  |  |  |  | Average PI and SLD degr by temperature | [7 empty] | CHP=Combined Heat & Power |  |  |  | 1.125 | 0.96 | average | 0 | < min, # > | 21 | [5 empty] | (First Solar was sometimes used by |  | Actual | Expected | Expected | Expected | Expected | Expected | Expected | Expected | 7-year | 0.70661 | -5.566% | 0.89715 | -1.719% | 0.85869 | 0.93789 | First 7 years: linear degr. |  | 7-yr | Subsequent years: linear degr. |  | post-7 | Squared deviation from straight-line fit, by year | [23 empty] | specific |  | RMS var.
Line# | EIA# | Name | 1st full yr | 1st kWh | Sector | Module type | Developer | (F)ix,(T)rkr | Slope/Tilt | State | Lat | Long | MWp | MWac | POA (by eqn.) | TMY2 Source | Annual T,air | Estim. Tmod | and C<40 | GHI | DHI | Kt | DF | Est.Clip | Degr Frac. | p50,Yr1 MWh | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 14 |  | Line # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Line # | Expected | Actual | Lifetime PI | Percentile Rank | Type | Lifetime Degr | Linest slope | Linest Int. |  | State | # systems | PI | Degr |  | Type | # systems | PI | SLD Degr | Size | PI | SLD | % of systems | Type | PI | SLD | # systems | ILR | 0.70953 | stdev | 3 | < max, # > | 6 | Name | Number | MWp | Avg PI | Avg SLD | developers other than FS) |  | 7-year MWh | yr 1 MWh | yr 2 MWh | yr 3 MWh | yr 4 MWh | yr 5 MWh | yr 6 MWh | yr 7 MWh | PI | Hot | Hot | Cold | Cold | Hot | Cold | slope | intercept | degr. | slope | intercept | degr | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | RMS variability | TMY2 variability | % explained variability | 1st 7 yrs | % explained
1 | 141 | Agua Fria PV-3 | 2003 | 2003 | Electric Utility | c-Si | Other utility | Tracker | 0 | AZ | 33.5567 | -112.2153 | 0.2576 | 0.25 | 2922 | Phoenix | 22.6 | 55.768 | H | 2117 | 566 | 0.678 | 0.26736 | 2.908% | 0.68722 | 572.0575 | 395 | 297 | 111 | 285 | 398 | 437 | 201 | 438 | 447 | 437 | 395 | 255 | 0 | 153 | 217 | 281 | 136 | 0 | 0 | 0 | 0 | 21 | 79 | 23 |  | 1 | 0.69049 | 0.52179 | 0.19599 | 0.50575 | 0.70982 | 0.7833 | 0.36209 | 0.793 | 0.81336 | 0.79916 | 0.72598 | 0.47103 | 0 | 0.28546 | 0.40691 | 0.52957 | 0.25759 | 0 | 0 | 0 | 0 | 0.040784 | 0.1542 | 1 | 12458.3757 | 4983 | 0.39997 | 99 | Tracker | -7.688% | -17.3211 | 424.5059 |  | CA | 30 | 0.79967 | -4.553% |  | H | 12 | 0.71726 | -5.384% | >5 MW,ac | 0.93821 | -2.043% | 23 | Commercial CHP | 0.73858 | -1.231% | 2 | 1.0304 | 0 |  |  |  |  | Conergy | 1 |  |  |  | CdSCdTe | 15 | 2124 | 572.0575 | 569.1972 | 566.3512 | 563.5194 | 560.7018 | 557.8983 | 555.1088 | 0.53843 | 0.39997 | -7.688% |  |  | 0.53843 |  | -0.53571 | 305.5714 | -0.1764% | -26.2426 | 573.6397 | -14.58% | 8093.5727 | 56.25 | 37235.2156 | 339.6122 | 9045.3686 | 18128.699 | 10164.9605 | 5520.7085 | 11999.9137 | 15822.3102 | 12106.4715 | 13.8975 | 54049.412 | 2834.7795 | 1369 | 16190.6912 | 72.0002 | 10256.0299 | 5629.4126 | 2380.1484 | 508.2372 | 610.0174 | 11868.1799 | 46.59% | 3.6% | 7.728% | 35.9% | 10.03%
2 | 56568 | Nellis Sunpower | 2008 | 2007 | Commercial Non-CHP | Si_IBT | SunPower | Tracker | 20 | NV | 36.26 | -115.05 | 14.2 | 13.2 | 3146.8088 | Las Vegas | 19.5 | 54.3391 | H | 2078 | 550 | 0.684 | 0.26468 | 6.541% | 0.43008 | 32000 | 32500 | 32000 | 31301 | 32125 | 32159 | 31758 | 31202 | 30428 | 19725 | 28213 | 26910 | 26474 | 24959 | 19180 | 19975 | 21723 | 23764 | [6 empty] | 17 |  | 2 | 1.0156 | 1.005 | 0.98801 | 1.0191 | 1.0253 | 1.0176 | 1.0048 | 0.98483 | 0.64163 | 0.92234 | 0.88416 | 0.87421 | 0.82832 | 0.63973 | 0.6696 | 0.73185 | 0.80464 | [6 empty] | 2 | 522774.6025 | 464396 | 0.88833 | 44 | Tracker | -2.917% | -808.723 | 34595.9191 |  | NJ | 16 | 0.88883 | -1.753% |  | M | 41 | 0.8337 | -3.589% | <5 MW,ac | 0.81155 | -3.43% | 77 | Commercial Non-CHP | 0.77254 | -6.296% | 9 | 1.0758 | 1 |  |  |  |  | Duke | 4 | 5.935 | 0.81371 | -4.412% | c-Si | 80 | 223045 | 32000 | 31840 | 31680.8 | 31522.396 | 31364.784 | 31207.9601 | 31051.9203 | 1.0108 | 0.88833 | -2.917% |  |  | 1.0108 |  | -125.7143 | 32366.4286 | -0.3938% | -829.7909 | 34735.0364 | -3.349% | 67229.0816 | 13225 | 473737.2245 | 68344.898 | 177361.3061 | 21274.3061 | 80899.6122 | 5434917.3028 | 56880529.8612 | 3153723.9435 | 1696932.5495 | 2877958.0248 | 1022617.3693 | 15507557.6013 | 5350768.0662 | 70022.7821 | 9830790.1674 | [6 empty] | 8.999% | 4.1% | 45.56% | 1.127% | 363.9%
3 | 56481 | SunE Alamosa1 | 2008 | 2007 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | CO | 37.6903 | -105.8805 | 9.2 | 8.2 | 2856.0962 | Alamosa | 5.1 | 37.7781 | C | 1926 | 518 | 0.644 | 0.26895 | 4.884% | 0.53257 | 19969.8246 | 17531 | 17455 | 17608 | 17797 | 17573 | 16907 | 16601 | 2638 | 2636 | 34876 | 15939 | 15517 | 14258 | 12321 | 13729 | 11357 | 13435 | [6 empty] | 17 |  | 3 | 0.87787 | 0.87846 | 0.89061 | 0.9047 | 0.8978 | 0.86811 | 0.85669 | 0.13682 | 0.1374 | 1.15 | 0.83918 | 0.82107 | 0.75824 | 0.65852 | 0.73747 | 0.61312 | 0.72894 | [6 empty] | 3 | 326241.1599 | 258178 | 0.79137 | 69 | Tracker | -1.801% | -276.0392 | 17671.2941 |  | CO | 8 | 0.83645 | -2.463% |  | C | 47 | 0.87829 | -2.113% | All | 0.84068 | -3.111% | 100 | All Commercial | 0.76636 | -5.375% | 11 | 1.122 | 1 |  |  |  |  | First Solar | 10 | 167.0364 | 0.91694 | -1.316% | HIT | 0 | 121472 | 19969.8246 | 19869.9755 | 19770.6256 | 19671.7725 | 19573.4136 | 19475.5465 | 19378.1688 | 0.88209 |  |  | 0.79137 | -1.801% |  | 0.88209 | -140.0357 | 17913.2857 | -0.8037% | 50.3091 | 13333.2909 | 0.361% | 58685.0625 | 31760.3316 | 13183.9605 | 197009.1633 | 129522.8686 | 27579.7194 | 110247.7156 | 123160357.7286 | 124324121.8235 | 442665533.2367 | 4211972.6046 | 2496400 | 73273.5683 | 2946777.9821 | 128828.7871 | 7735275.7104 | 567830.7521 | [6 empty] | 42.52% | 3.1% | 7.291% | 1.642% | 188.9%
4 | 56900 | Atlantic Cty ConvCtr | 2009 | 2008 | Commercial Non-CHP | c-Si | Unknown | Fixed | 10 | NJ | 39.36 | -74.44 | 2.4 | 2 | 1570.575 | Atlantic City | 11.7 | 34.8225 | C | 1486 | 672 | 0.509 | 0.45222 | 0% | 1 | 3015.504 | 2767 | 3028 | 3069 | 3066 | 2850 | 2979 | 2982 | 3062 | 2990 | 2899 | 3117 | 3054 | 2986 | 3094 | 2817 | 2075 | [7 empty] | 16 |  | 4 | 0.91759 | 1.0092 | 1.028 | 1.0322 | 0.96426 | 1.013 | 1.0191 | 1.0517 | 1.0321 | 1.0057 | 1.0868 | 1.0702 | 1.0516 | 1.0951 | 1.0021 | 0.74184 | [7 empty] | 4 | 46480.3008 | 46835 | 1.0076 | 10 | Fixed | -0.5896% | -17.3103 | 3074.325 |  | NC | 7 | 0.79658 | -4.01% |  | All | 100 | 0.84068 | -3.111% |  |  |  |  | Electric Utility | 0.84578 | -3.173% | 24 | 1.2 | 1 |  |  |  |  | MMA | 6 | 12.8785 | 0.77413 | -4.115% | Si_IBT | 5 | 20741 | 3015.504 | 3000.4265 | 2985.4243 | 2970.4972 | 2955.6447 | 2940.8665 | 2926.1622 | 0.99743 |  |  | 1.0076 | -0.5896% |  | 0.99743 | 11.7143 | 2916.1429 | 0.3961% | -55.5152 | 3546.0242 | -1.909% | 25875.0204 | 7819.6122 | 13856.6531 | 10609 | 15553.6531 | 55.1837 | 260.5918 | 1592.2518 | 3179.5929 | 8440.598 | 32993.9703 | 30330.8612 | 26138.0707 | 105747.1565 | 10754.3185 | 339634.6476 | [7 empty] | 6.794% | 2.75% | 40.48% | 3.471% | 79.23%
5 | 56862 | MMA Bolthouse | 2009 | 2008 | IPP Non-CHP | c-Si | MMA | Tracker | 15 | CA | 34.56 | -117.69 | 1.9055 | 1.5 | 3122.8875 | Daggett | 19.8 | 54.4613 | H | 2138 | 489 | 0.696 | 0.22872 | 11.14% | 0.2375 | 4522.5032 | 2526 | 2586.87 | 4298.58 | 4231 | 4053 | 4089 | 2259 | 3778 | 3270 | 1886 | 3325 | 2779 | 1548 | 857 | 93 | 67 | [7 empty] | 16 |  | 5 | 0.55854 | 0.57487 | 0.96006 | 0.94972 | 0.91434 | 0.92709 | 0.51475 | 0.86521 | 0.75263 | 0.43627 | 0.773 | 0.64932 | 0.36351 | 0.20226 | 0.022059 | 0.015972 | [7 empty] | 5 | 69708.848 | 41646.45 | 0.59743 | 95 | Tracker | -7.905% | -214.2275 | 4423.8367 |  | PA | 6 | 0.85425 | -2.202% | [9 empty] | Industrial Non-CHP | 0.92061 | -1.434% | 2 | 1.2703 | 1 |  |  |  |  | NextEra | 0 | 0 |  |  | Unknown | 0 | 24043.45 | 4522.5032 | 4499.8907 | 4477.3913 | 4455.0043 | 4432.7293 | 4410.5656 | 4388.5128 | 0.77095 | 0.59743 | -7.905% |  |  | 0.77095 |  | 69.9171 | 3155.11 | 2.056% | -358.4727 | 6108.6364 | -18.05% | 488638.9465 | 501369.1941 | 871830.3706 | 633968.5633 | 300637.5897 | 264594.1327 | 1919693.3809 | 288525.2393 | 150247.8549 | 406928.0083 | 1344587.8268 | 944854.6922 | 9902.0592 | 54297.4731 | 407740.2975 | 93680.5144 | [7 empty] | 28.3% | 2.8% | 9.894% | 24.56% | 11.4%
6 | 56944 | Copper Mtn10 (FS) | 2009 | 2008 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 25 | NV | 35.79 | -114.99 | 12.4 | 10 | 2337.6 | Las Vegas | 19.5 | 48.324 | M | 2078 | 550 | 0.684 | 0.26468 | 1.704% | 0.80263 | 23188.992 | 21661 | 21146 | 21546 | 21245 | 20375 | 19869 | 19885 | 19061 | 19321 | 19595 | 22562 | 21953 | 18686 | 18948 | 19201 | 17988 | [7 empty] | 16 |  | 6 | 0.93411 | 0.91648 | 0.93851 | 0.93005 | 0.89644 | 0.87857 | 0.8837 | 0.85134 | 0.86729 | 0.88401 | 1.023 | 1.0004 | 0.85577 | 0.87213 | 0.88822 | 0.83629 | [7 empty] | 6 | 357429.9099 | 323042 | 0.90379 | 38 | Fixed | -0.7842% | -158.9529 | 21541.225 |  | AZ | 6 | 0.69425 | -5.073% | [9 empty] | IPP Non-CHP | 0.84918 | -2.745% | 63 | 1.24 | 1 |  |  |  |  | NRG | 1 | 26.4 | 0.92423 | -1.575% |  | 100 | 145727 | 23188.992 | 23073.047 | 22957.6818 | 22842.8934 | 22728.6789 | 22615.0355 | 22501.9604 | 0.91132 | [6 empty] | -323.3214 | 22111.4286 | -1.541% | -129.0545 | 21204.1273 | -0.6544% | 16156.2258 | 101624.3316 | 163649.1441 | 182207.0204 | 14357.1747 | 91506.25 | 1355.8176 | 1233634.2955 | 520759.0413 | 101494.3749 | 7714354.7507 | 5278631.5689 | 706302.7203 | 201927.6777 | 4530.5137 | 1325387.0284 | [7 empty] | 5.203% | 3% | 57.66% | 1.372% | 218.7%
7 | 56813 | CSU Fresno MMA | 2008 | 2007 | IPP Non-CHP | c-Si | MMA | Fixed | 2 | CA | 36.8098 | -119.7417 | 1.173 | 1 | 1937.286 | Fresno | 17.4 | 43.2484 | M | 1910 | 578 | 0.634 | 0.30262 | 0% | 1 | 1547 | 1442 | 1655 | 1123 | 981 | 1556 | 1564 | 1453 | 1466 | 1445 | 1452 | 1294 | 1485 | 1149 | 1059 | 592 | 1094 | 1438 | [6 empty] | 17 |  | 7 | 0.93213 | 1.0752 | 0.73324 | 0.64374 | 1.0262 | 1.0366 | 0.96791 | 0.98148 | 0.97228 | 0.9819 | 0.87945 | 1.0143 | 0.78877 | 0.73064 | 0.4105 | 0.7624 | 1.0072 | [6 empty] | 7 | 25272.8847 | 22248 | 0.88031 | 49 | Fixed | -1.663% | -21.9412 | 1506.1765 |  | FL | 4 | 0.90603 | -3.803% | [9 empty] | All | 0.84068 | -3.111% | 100 | 1.173 | 1 |  |  |  |  | Other utility | 4 | 7.3576 | 0.66938 | -4.965% |  |  | 9774 | 1547 | 1539.265 | 1531.5687 | 1523.9108 | 1516.2913 | 1508.7098 | 1501.1663 | 0.91621 | [6 empty] | 10.1429 | 1355.7143 | 0.7291% | -45.9364 | 1817.3273 | -3.628% | 5797.7347 | 77841 | 69244.1633 | 172462.2245 | 22371.6122 | 21735.1837 | 690.9388 | 261.2631 | 1689.21 | 8842.8377 | 324.9826 | 47921.1901 | 5062.9693 | 13275.2294 | 287598.1885 | 135.8284 | 161275.2583 | [6 empty] | 17.55% | 3% | 17.1% | 16.47% | 18.22%
8 | 10823 | Deer Island | 2011 | 2008 | Commercial CHP | c-Si | Unknown | Fixed | 15 | MA | 42.353 | -70.963 | 0.736 | 0.666 | 1534.05 | Boston | 10.7 | 33.551 | C | 1432 | 652 | 0.509 | 0.45531 | 0% | 1 | 903.2486 | 646 | 879 | 881 | 0 | 835 | 872 | 826 | 799 | 808 | 1123 | 760 | 794 | 628 | 625 | 621 | [8 empty] | 15 |  | 8 | 0.7152 | 0.97804 | 0.9852 | 0 | 0.94316 | 0.98991 | 0.9424 | 0.91617 | 0.93115 | 1.15 | 0.88466 | 0.92888 | 0.73837 | 0.73854 | 0.7375 | [8 empty] | 8 | 13084.6461 | 11097 | 0.84809 | 57 | Fixed | 0.2276% | 1.6821 | 726.3429 |  | NM | 4 | 0.95293 | 0.1957% | [13 empty] | 1.1051 | 3 |  |  |  |  | PG&E | 4 | 63.3 | 0.89293 | -4.26% |  |  | 4939 | 903.2486 | 898.7324 | 894.2387 | 903.2486 | 885.3187 | 880.8921 | 876.4876 | 0.79123 |  |  | 0.84809 | 0.2276% |  | 0.79123 | 17.1429 | 637 | 2.46% | -33.85 | 1148.35 | -4.362% | 66.3061 | 43145.2245 | 37083.7551 | 497831.0408 | 12608.0816 | 17461.7347 | 4761 | 6170.1025 | 1274.49 | 98062.9225 | 256 | 2688.4225 | 6448.09 | 2445.3025 | 384.16 | [8 empty] | 29.83% | 2.9% | 9.721% | 41.94% | 6.915%
9 | 56815 | Denver airport MMA | 2009 | 2008 | IPP Non-CHP | c-Si | MMA | Tracker | 0 | CO | 39.903 | -104.6593 | 2 | 1.9 | 2337.6 | Boulder | 10.2 | 39.024 | C | 1689 | 562 | 0.583 | 0.33274 | 0% | 1 | 3553.152 | 3255 | 3449 | 3287 | 3468 | 1469 | 2687 | 3027 | 3205 | 2812 | 2539 | 2092 | 2284 | 1463 | 275 | 1595 | 1541 | [7 empty] | 16 |  | 9 | 0.91609 | 0.97557 | 0.93441 | 0.99082 | 0.42181 | 0.77542 | 0.87793 | 0.93423 | 0.82379 | 0.74755 | 0.61904 | 0.67925 | 0.43727 | 0.082607 | 0.48153 | 0.46757 | [7 empty] | 9 | 54767.4862 | 38448 | 0.70202 | 87 | Tracker | -5.945% | -147.2294 | 3654.45 |  | NV | 4 | 0.88115 | -1.759% | [13 empty] | 1.0526 | 1 |  |  |  |  | SunEdison | 14 | 35.2 | 0.78848 | -3.819% |  |  | 20642 | 3553.152 | 3535.3862 | 3517.7093 | 3500.1208 | 3482.6202 | 3465.2071 | 3447.881 | 0.84246 |  |  | 0.70202 | -5.945% |  | 0.84246 | -143.7857 | 3524 | -4.76% | -244.6364 | 4896.6182 | -11.74% | 15678.6173 | 45186.6122 | 37774.699 | 269509.3061 | 1785086.8622 | 661.2245 | 259590.25 | 70475.7689 | 13714.5392 | 7875.7557 | 12909.0912 | 104340.7458 | 64183.9193 | 1432112.6483 | 135370.478 | 311993.3359 | 544348.84 | [6 empty] | 22.82% | 5.1% | 22.35% | 19.91% | 25.61%
10 | 56667 | Lanai Sunpower | 2009 | 2008 | IPP Non-CHP | Si_IBT | SunPower | Tracker | 0 | HI | 20.766 | -156.9 | 1.4784 | 1.2 | 2739.375 | Kahului | 24.2 | 56.0105 | H | 2004.4 | 579 | 0.581 | 0.28886 | 7.233% | 0.39335 | 3077.9179 | 1390 | 1770 | 1826 | 2350 | 1752 | 1767 | 2017 | 2345 | 2051 | 1342 | 1466 | 869 | 0 | 145 | 0 | 0 | [7 empty] | 16 |  | 10 | 0.4516 | 0.57795 | 0.59924 | 0.77507 | 0.58074 | 0.58866 | 0.67532 | 0.78909 | 0.69362 | 0.45613 | 0.50078 | 0.29834 | 0 | 0.050282 | 0 | 0 | [7 empty] | 10 | 47442.3349 | 21090 | 0.44454 | 97 | Tracker | -9.915% | -137.5088 | 2486.95 |  | MA | 3 | 0.87955 | -0.206% | [13 empty] | 1.232 | 1 |  |  |  |  | SunPower | 4 | 26.7784 | 0.7694 | -5.859% |  |  | 12872 | 3077.9179 | 3062.5283 | 3047.2157 | 3031.9796 | 3016.8197 | 3001.7356 | 2986.7269 | 0.60646 | 0.44454 | -9.915% |  |  | 0.60646 |  | 64.3214 | 1581.5714 | 3.56% | -295.2788 | 4419.2061 | -28.85% | 65481.1543 | 3574.3316 | 2648.5727 | 261267.0204 | 22854.9605 | 40200.25 | 219.6747 | 82957.9642 | 83696.2433 | 15479.884 | 86942.777 | 47.0679 | 337075.2476 | 19684.9403 | 99.5157 | 93180.3375 | 360640.2844 | [6 empty] | 22.35% | 5% | 22.37% | 12.94% | 38.64%
11 | 56993 | MF Mesa Ln | 2009 | 2009 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | PA | 40.15 | -74.78 | 3.1 | 3 | 1643.625 | Philadelphia | 12.4 | 36.0655 | C | 1455 | 671.5 | 0.501 | 0.46151 | 0% | 1 | 4076.19 | 3562 | 4053 | 3867 | 3991 | 3900 | 3699 | 3878 | 4021 | 3598 | 3223 | 3729 | 3527 | 3568 | 3458 | 3079 | 3402 | [7 empty] | 16 |  | 11 | 0.87386 | 0.99931 | 0.95824 | 0.99394 | 0.97615 | 0.9305 | 0.98043 | 1.0217 | 0.9188 | 0.82718 | 0.96185 | 0.91432 | 0.92959 | 0.90546 | 0.81027 | 0.89977 | [7 empty] | 11 | 62829.4764 | 58555 | 0.93197 | 28 | Fixed | -1.127% | -41.4956 | 4012.4 |  | HI | 2 | 0.72746 | -5.64% | [13 empty] | 1.0333 | 0 |  |  |  |  | Unknown | 52 | 293.47 | 0.86186 | -2.636% |  |  | 26950 | 4076.19 | 4055.8091 | 4035.53 | 4015.3524 | 3995.2756 | 3975.2992 | 3955.4227 | 0.95877 |  |  | 0.93197 | -1.127% |  | 0.95877 | 9.75 | 3811 | 0.2536% | -65.1212 | 4297.1939 | -1.835% | 66951.5625 | 49506.25 | 715.5625 | 19881 | 1620.0625 | 29070.25 | 1.5625 | 59915.1715 | 12792.2955 | 178913.6185 | 21945.28 | 126.8012 | 13778.4912 | 5256.6894 | 58262.2563 | 21534.2284 | 10176950.6844 | [6 empty] | 21.7% | 3.3% | 15.21% | 4.021% | 82.07%
12 | 56883 | Pennsauken | 2008 | 2008 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | NJ | 39.9894 | -75.04 | 2.4 | 1.5 | 1643.625 | Philadelphia | 12.4 | 36.0655 | C | 1455 | 671.5 | 0.501 | 0.46151 | 5.496% | 0.49213 | 3155.76 | 2660 | 3018 | 2592 | 2454 | 2490 | 2523 | 2402 | 2352 | 2308 | 2369 | 2041 | 2292 | 2188 | 2086 | 2156 | 1851 | [7 empty] | 16 |  | 12 | 0.8429 | 0.96115 | 0.82963 | 0.78941 | 0.80501 | 0.81978 | 0.78439 | 0.77192 | 0.76128 | 0.78533 | 0.68 | 0.76746 | 0.73632 | 0.70552 | 0.73286 | 0.63235 | [7 empty] | 12 | 48642.1752 | 37782 | 0.77673 | 72 | Fixed | -2.171% | -51.8235 | 2801.875 |  | TX | 2 | 0.90922 | -1.272% | [13 empty] | 1.6 | 0 |  |  |  |  | totals&avgs | 99 | 638.3559 | 0.84068 | -3.111% |  |  | 18139 | 3155.76 | 3139.9812 | 3124.2813 | 3108.6599 | 3093.1166 | 3077.651 | 3062.2628 | 0.83353 |  |  | 0.77673 | -2.171% |  | 0.83353 | -66.6429 | 2857.8571 | -2.539% | -46.8667 | 2743.4667 | -2.126% | 17217.1888 | 86100.3265 | 4346.5765 | 18847.3673 | 1200.1276 | 4225 | 113.2704 | 273.3511 | 186.7778 | 8873.64 | 34944.0711 | 12306.2044 | 2894.44 | 1.7778 | 13347.9511 | 20334.76 | 3789770.6711 | [6 empty] | 20.58% | 3.3% | 16.03% | 5.3% | 62.26%
13 | 56915 | SAS Solar Farm | 2009 | 2008 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | NC | 35.81 | -78.75 | 2.4 | 2 | 2081.925 | Raleigh | 15.2 | 42.1235 | M | 1626 | 728 | 0.534 | 0.44772 | 3.736% | 0.61754 | 3797.4312 | 1539 | 2435 | 3579 | 3500 | 3134 | 3375 | 3250 | 3290 | 3049 | 2540 | 1837 | 1977 | 1820 | 1928 | 1735 | 1692 | [7 empty] | 16 |  | 13 | 0.40527 | 0.64445 | 0.95198 | 0.93564 | 0.84201 | 0.91131 | 0.88197 | 0.89731 | 0.83576 | 0.69974 | 0.50861 | 0.55013 | 0.50898 | 0.5419 | 0.4901 | 0.48036 | [7 empty] | 13 | 58532.7509 | 40680 | 0.695 | 88 | Tracker | -3.313% | -85.6559 | 3270.575 |  | DE | 1 | 1.0212 | -2.219% | [13 empty] | 1.2 | 1 |  |  |  |  | medians |  |  | 0.87759 | -2.33% |  |  | 20812 | 3797.4312 | 3778.444 | 3759.5518 | 3740.7541 | 3722.0503 | 3703.44 | 3684.9228 | 0.79476 | [6 empty] | 234.5714 | 2034.8571 | 8.214% | -197.1636 | 4579.1818 | -8.529% | 533525.898 | 4761 | 706320.1837 | 277578.449 | 5433.7959 | 4527.3673 | 182207.0204 | 83017.3253 | 59678.0483 | 4562.3884 | 328766.7094 | 55799.0294 | 38437.3848 | 11904.7937 | 12830.7107 | 71522.2086 | 1506510.76 | [6 empty] | 18.81% | 3.5% | 18.61% | 16.65% | 21.03%
14 | 56875 | Sacramento Soleil | 2009 | 2008 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 45 | CA | 38.4498 | -121.1647 | 1.2364 | 1 | 1988.7862 | Sacramento | 16 | 42.2312 | M | 1793 | 572 | 0.608 | 0.31902 | 0% | 1 | 1967.1228 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1686; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1744; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1780; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1709; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1778; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1692; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1730; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 1683; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 1710; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 1537; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 1446; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 1360; Median age 14: 12 |  | 14 | 0.85709 | 0.89103 | 0.91399 | 0.88194 | 0.92216 | 0.88197 | 0.90631 | 0.88612 | 0.90486 | 0.8174 | 0.77287 | 0.73056 | [11 empty] | 14 | 22967.0215 | 19855 | 0.8645 | 53 | Fixed | -1.72% | -28.7098 | 1841.197 |  | IL | 1 | 1.0086 | -1.024% | [13 empty] | 1.2364 | 1 | [11 empty] | 12119 | 1967.1228 | 1957.2872 | 1947.5007 | 1937.7632 | 1928.0744 | 1918.4341 | 1908.8419 | 0.8934 | [6 empty] | 0.92857 | 1727.5714 | 0.05365% | -78.1143 | 2319.7524 | -4.951% | 1806.25 | 212.3265 | 2464.4133 | 496.6531 | 2096.3316 | 1692.7347 | 16.5765 | 140.1405 | 8700.4477 | 2.5906 | 210.1119 | 500.907 | [11 empty] | 2.363% | 3.4% | 143.9% | 2.046% | 166.2%
15 | 56500 | Western 102 | 2010 | 2010 | Industrial Non-CHP | c-Si | Unknown | Fixed | 21 | NV | 39.5603 | -119.5108 | 1.575 | 1 | 2118.45 | Reno | 10.4 | 37.595 | C | 1848 | 511 | 0.633 | 0.27652 | 6.446% | 0.43537 | 2669.247 | 1694 | 1247 | 2770 | 2647 | 2560 | 2501 | 2546 | 2515 | 2508 | 2443 | 2572 | 2209 | 1452 | 1373 | 1261 | 1337 | [7 empty] | 16 |  | 15 | 0.63464 | 0.46952 | 1.0482 | 1.0067 | 0.9785 | 0.96075 | 0.98295 | 0.97586 | 0.97803 | 0.95747 | 1.0131 | 0.87449 | 0.5777 | 0.54901 | 0.50676 | 0.54 | [7 empty] | 15 | 41143.1732 | 33635 | 0.81751 | 63 | Fixed | -2.331% | -49.5779 | 2523.6 |  | MD | 1 | 0.83875 | -4.149% | [13 empty] | 1.575 | 0 | [11 empty] | 15965 | 2669.247 | 2655.9008 | 2642.6213 | 2629.4082 | 2616.2611 | 2603.1798 | 2590.1639 | 0.86734 |  |  | 0.81751 | -2.331% |  | 0.86734 | 173.3571 | 1587.2857 | 7.901% | -173.7576 | 4019.8121 | -8.595% | 4441.2704 | 471969 | 439095.5561 | 134165.2245 | 11220.8622 | 15984.1837 | 64915.7602 | 13167.9102 | 2704.6303 | 25844.9468 | 214851.9141 | 75228.8535 | 95458.5286 | 45884.2364 | 23240.5405 | 9469.0592 | [7 empty] | 15.27% | 3.3% | 21.62% | 17.71% | 18.64%
16 | 56322 | Wild Horse | 2011 | 2011 | Electric Utility | c-Si | Unknown | Fixed | 37 | WA | 47.036 | -120.206 | 0.5 | 0.5 | 1753.2 | Yakima | 9.9 | 34.38 | C | 1501.5 | 554 | 0.567 | 0.36896 | 0% | 1 | 701.28 | 840 | 794 | 762 | 729 | 790 | 727 | 481 | 488 | 389 | 95 | 484 | 556 | 637 | 666 | 676 | [8 empty] | 15 |  | 16 | 1.15 | 1.1379 | 1.0975 | 1.0553 | 1.1493 | 1.063 | 0.70683 | 0.72072 | 0.5774 | 0.14172 | 0.72564 | 0.83778 | 0.96465 | 1.0136 | 1.034 | [8 empty] | 16 | 10158.8867 | 9114 | 0.89715 | 41 | Fixed | -3.185% | -19.6679 | 764.9429 |  | OH | 1 | 0.92341 | -2.33% | [13 empty] | 1 | 0 | [11 empty] | 5123 | 730.4348 | 697.7736 | 694.2847 | 690.8133 | 687.3592 | 683.9224 | 680.5028 | 1.053 |  |  | 0.89715 | -3.185% |  | 1.053 | -42.25 | 900.8571 | -5.611% | 37.85 | 80.5389 | 7.617% | 346.2258 | 499.8418 | 146.5829 | 8.1633 | 10078.7258 | 6342.9847 | 15402.5829 | 10953.9482 | 1036.1246 | 132524.3126 | 166.1235 | 452.0348 | 4148.7912 | 3087.0371 | 767.9057 | [8 empty] | 18.33% | 2.3% | 12.55% | 9.357% | 24.58%
17 | 57280 | Aqua Ingrams Mill | 2010 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 20 | PA | 39.965 | -75.658 | 1.2 | 1 | 1643.625 | Philadelphia | 12.4 | 36.0655 | C | 1455 | 671.5 | 0.501 | 0.46151 | 0% | 1 | 1577.88 | 1369 | 1314 | 0 | 1343 | 1266 | 1257 | 1079 | 1231 | 1153 | 1346 | 1110 | 1345 | 818 | 769 | [9 empty] | 14 |  | 17 | 0.86762 | 0.83695 | 0 | 0.86404 | 0.81859 | 0.81686 | 0.70471 | 0.80802 | 0.76063 | 0.89241 | 0.73964 | 0.90073 | 0.55056 | 0.52018 | [9 empty] | 17 | 21386.5478 | 15400 | 0.72008 | 86 | Fixed | -0.5066% | -5.5868 | 1141.9011 |  | VT | 1 | 0.94377 | -1.098% | [13 empty] | 1.2 | 0 | [11 empty] | 7628 | 1577.88 | 1569.9906 | 1577.88 | 1554.3299 | 1546.5583 | 1538.8255 | 1531.1314 | 0.70004 |  |  | 0.72008 | -0.5066% |  | 0.70004 | 10.0714 | 1049.4286 | 0.9285% | -46.369 | 1593.25 | -4.191% | 95790.25 | 59745.3265 | 1165628.699 | 64153.6531 | 27627.1888 | 21651.0204 | 1675.148 | 75.7314 | 525.7194 | 46846.4797 | 718.7506 | 94974.0319 | 29739.8237 | 30654.1736 | [9 empty] | 31.11% | 3.3% | 10.61% | 41.57% | 7.939%
18 | 57081 | Calpine Vineland Solar LLC | 2010 | 2009 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | NJ | 39.4636 | -75.0667 | 4.3 | 4.1 | 1680.15 | Atlantic City | 11.7 | 35.637 | C | 1486 | 672 | 0.509 | 0.45222 | 0% | 1 | 5779.716 | 7567 | 5492 | 6862 | 5372 | 5514 | 5400 | 5605 | 5483 | 5086 | 5214 | 4972 | 5490 | 5513 | 5640 | 5365 | [8 empty] | 15 |  | 18 | 1.15 | 0.95499 | 1.15 | 0.94354 | 0.97335 | 0.95801 | 0.99938 | 0.98254 | 0.91598 | 0.94375 | 0.90447 | 1.0037 | 1.013 | 1.0415 | 0.99573 | [8 empty] | 18 | 83726.158 | 84575 | 1.0101 | 8 | Fixed | -1.466% | -83.2714 | 6304.5048 |  | WA | 1 | 0.89715 | -3.185% | [13 empty] | 1.0488 | 1 | [11 empty] | 41812 | 6580 | 5750.8174 | 5966.9565 | 5693.453 | 5664.9858 | 5636.6608 | 5608.4775 | 1.0223 |  |  | 1.0101 | -1.466% |  | 1.0223 | -264.9286 | 7032.8571 | -4.339% | 10.6833 | 5256.7056 | 0.1988% | 638515.148 | 1022121 | 389286.8622 | 361372.7347 | 37719.1888 | 1873.6531 | 182024.1276 | 19832.463 | 71211.8875 | 22361.8793 | 161782.716 | 11044.8423 | 13785.369 | 54628.6741 | 2699.3798 | [8 empty] | 7.919% | 3% | 37.88% | 10.27% | 29.22%
19 | 57011 | Chuckawalla SunE | 2009 | 2006 | IPP Non-CHP | c-Si | SunEdison | Fixed | 20 | CA | 33.565 | -114.904 | 1.2 | 1 | 2374.125 | Daggett | 19.8 | 48.8955 | M | 2138 | 489 | 0.696 | 0.22872 | 0.02968% | 0.99618 | 2279.16 | 2078 | 2082 | 2134 | 1734 | 2062 | 2005 | 1909 | 3184 | 1764 | 1529 | 1807 | 1653 | 1479 | 484 | 1152 | 1389 | [7 empty] | 16 |  | 19 | 0.91174 | 0.91808 | 0.94574 | 0.77233 | 0.92304 | 0.90204 | 0.86316 | 1.15 | 0.80564 | 0.70182 | 0.83359 | 0.76638 | 0.68915 | 0.22666 | 0.54219 | 0.65702 | [7 empty] | 19 | 35130.4599 | 28445 | 0.8097 | 65 | Fixed | -3.995% | -72.475 | 2393.85 |  | NY | 1 | 1.055 | -1.09% | [13 empty] | 1.2 | 3 | [11 empty] | 14004 | 2279.16 | 2267.7642 | 2256.4254 | 2245.1433 | 2233.9175 | 2222.7479 | 2211.6342 | 0.89102 | [6 empty] | -26.1786 | 2105.2857 | -1.3% | -155.2 | 3419.8 | -9.492% | 1.2258 | 845.148 | 11502.5625 | 71060.3265 | 7675.0115 | 3224.6173 | 169.9298 | 1011633.64 | 67081 | 114785.44 | 8911.36 | 9139.36 | 5898.24 | 582169 | 3624.04 | 204665.76 | [7 empty] | 20.39% | 2.2% | 10.79% | 5.807% | 37.88%
20 | 56929 | DeSoto | 2010 | 2009 | Electric Utility | c-Si | Unknown | Tracker | 0 | FL | 27.32 | -81.802 | 27.6 | 25 | 2301.075 | Tampa | 22.4 | 50.9525 | H | 1791.5 | 717 | 0.546 | 0.40022 | 2.595% | 0.71553 | 48267.3492 | 53341 | 51845 | 52048 | 49827 | 47421 | 50036 | 48650 | 48200 | 46882 | 45754 | 40585 | 43742 | 37524 | 33459 | 28061 | [8 empty] | 15 |  | 20 | 1.1051 | 1.0795 | 1.0892 | 1.048 | 1.0024 | 1.063 | 1.0387 | 1.0343 | 1.011 | 0.99167 | 0.88406 | 0.95762 | 0.82562 | 0.73988 | 0.62363 | [8 empty] | 20 | 699210.775 | 677375 | 0.96877 | 17 | Tracker | -3.23% | -1482.4143 | 57017.6476 |  | OR | 1 | 0.73785 | -4.012% | [13 empty] | 1.104 | 1 | [11 empty] | 353168 | 48267.3492 | 48026.0125 | 47785.8824 | 47546.953 | 47309.2182 | 47072.6721 | 46837.3088 | 1.0611 | 0.96877 | -3.23% |  |  | 1.0611 |  | -797.0714 | 53640.8571 | -1.567% | -2455.1167 | 68434.8389 | -5.926% | 247222.0459 | 40688.6531 | 637374.1276 | 391339.6122 | 4992990.25 | 1386674.4694 | 346500.4133 | 352723.8089 | 295078.3112 | 3498125.9963 | 711585.9753 | 22739175.0704 | 1011387.7927 | 365064.3534 | 12581839.5857 | [8 empty] | 4.027% | 4.8% | 119.2% | 2.125% | 225.9%
21 | 57191 | Exelon Chicago | 2010 | 2009 | IPP Non-CHP | Si_IBT | SunPower | Tracker | 0 | IL | 41.68 | -87.65 | 10 | 9 | 1862.775 | Chicago | 9.4 | 34.6945 | C | 1431.4 | 665.5 | 0.505 | 0.46493 | 0.0416% | 0.99465 | 14157.09 | 14145 | 14062 | 15080 | 14293 | 14527 | 14126 | 14102 | 14328 | 13701 | 14091 | 13826 | 13176 | 13517 | 12586 | 11674 | 12865 | [7 empty] | 16 |  | 21 | 0.99915 | 0.99827 | 1.0759 | 1.0249 | 1.0469 | 1.0231 | 1.0265 | 1.0482 | 1.0074 | 1.0413 | 1.0268 | 0.98346 | 1.014 | 0.94889 | 0.88455 | 0.97969 | [7 empty] | 21 | 218214.2028 | 220099 | 1.0086 | 9 | Tracker | -1.024% | -141.5868 | 14959.675 |  | Total | 100 | 0.84068 | -3.111% | <avg degr | [12 empty] | 1.1111 | 1 | [11 empty] | 100335 | 14157.09 | 14086.3046 | 14015.873 | 13945.7937 | 13876.0647 | 13806.6844 | 13737.6509 | 1.0278 |  |  | 1.0086 | -1.024% |  | 1.0278 | -19.7857 | 14412.7143 | -0.1379% | -228.2303 | 16011.2485 | -1.705% | 61468.5765 | 96809.8776 | 528009.8418 | 1646.0408 | 45460.3316 | 28224 | 29657.7602 | 20333.0316 | 65626.0188 | 131083.4939 | 105810.2327 | 9309.326 | 223488.2648 | 52911.1521 | 835019.3637 | 255465.9177 | [7 empty] | 2.868% | 4.3% | 149.9% | 2.346% | 183.3%
22 | 56877 | Hall's Warehouse | 2009 | 2009 | IPP Non-CHP | CdSCdTe | Unknown | Fixed | 5 | NJ | 40.5737 | -74.3944 | 1.8 | 1.6 | 1461 | Newark | 12.7 | 35.008 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 2103.84 | 1871 | 2079 | 1918 | 2040 | 1869 | 1280 | 1508 | 1456 | 1782 | 1648 | 1557 | 1448 | 1358 | 1707 | 1594 | 1428 | [7 empty] | 16 |  | 22 | 0.88933 | 0.99316 | 0.92085 | 0.98435 | 0.90637 | 0.62385 | 0.73867 | 0.71678 | 0.88168 | 0.81948 | 0.77812 | 0.72728 | 0.6855 | 0.86601 | 0.81274 | 0.73176 | [7 empty] | 22 | 32428.1168 | 26543 | 0.81852 | 61 | Fixed | -1.951% | -32.6838 | 1936.75 |  | Count | 20 |  | -2.33% | <median degr | [12 empty] | 1.125 | 0 | [11 empty] | 12565 | 2103.84 | 2093.3208 | 2082.8542 | 2072.4399 | 2062.0777 | 2051.7673 | 2041.5085 | 0.86609 |  |  | 0.81852 | -1.951% |  | 0.86609 | -97.7143 | 2185.8571 | -5.299% | -6.7152 | 1625.8242 | -0.4336% | 47151.0204 | 7844.898 | 639.3673 | 60025 | 29485.7959 | 102125.898 | 37.7347 | 13479.9136 | 46920.8111 | 7979.3617 | 25.426 | 9456.0891 | 32590.0962 | 30690.7929 | 4747.6276 | 8168.8731 | [7 empty] | 9.547% | 2.6% | 27.23% | 10.47% | 24.83%
23 | 57009 | Kohl's San Bernardino SunE | 2009 | 2009 | IPP Non-CHP | c-Si | SunEdison | Fixed | 10 | CA | 34.0947 | -117.2668 | 1.2 | 1 | 2144.0175 | San Bernardino (Meteonorm) | 18.2 | 45.585 | M | 1921.2 | 600 | 0.62 | 0.3123 | 0.02993% | 0.99615 | 2058.2568 | 1832 | 1798 | 4049 | 1825 | 1762 | 1610 | 1918 | 859 | 0 | 1014 | 1368 | 1455 | 1455 | 1626 | 1049 | 944 | [7 empty] | 16 |  | 23 | 0.89007 | 0.87794 | 1.15 | 0.90011 | 0.8734 | 0.80207 | 0.96031 | 0.43225 | 0 | 0.51538 | 0.6988 | 0.74698 | 0.75073 | 0.84318 | 0.5467 | 0.49445 | [7 empty] | 23 | 31725.5076 | 24564 | 0.77427 | 74 | Fixed | -5.584% | -88.1912 | 2284.875 | [18 empty] | 1.2 | 0 | [11 empty] | 14794 | 2058.2568 | 2047.9655 | 3520.8696 | 2027.5371 | 2017.3994 | 2007.3124 | 1997.2758 | 0.9437 | [6 empty] | -85.8929 | 2457 | -3.983% | 12.7515 | 1022.1576 | 1.091% | 290636.5115 | 237377.7602 | 3421310.8176 | 83191.0408 | 70509.2156 | 109986.9847 | 3875.0625 | 70314.9682 | 1292589.8426 | 18407.0889 | 42261.3921 | 78301.6066 | 71327.8417 | 180898.1335 | 27037.3246 | 79626.5785 | [7 empty] | 40.14% | 2.2% | 5.48% | 36.72% | 5.991%
24 | 57005 | Mariani Packing SunE | 2009 | 2009 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | CA | 38.4 | -121.964 | 1.1 | 1 | 2483.7 | Sacramento | 16 | 45.91 | M | 1793 | 572 | 0.608 | 0.31902 | 1.833% | 0.78939 | 2076.3732 | 1996 | 1132 | 1986 | 2008 | 2142 | 1991 | 2010 | 1863 | 1689 | 1386 | 1753 | 1767 | 1566 | 545 | 891 | 1253 | [7 empty] | 16 |  | 24 | 0.96129 | 0.54792 | 0.96611 | 0.98172 | 1.0525 | 0.98322 | 0.99759 | 0.92928 | 0.84672 | 0.69831 | 0.88766 | 0.89924 | 0.80096 | 0.28015 | 0.46031 | 0.65058 | [7 empty] | 24 | 32004.7497 | 25978 | 0.81169 | 64 | Tracker | -3.556% | -58.7765 | 2123.225 | [18 empty] | 1.1 | 0 | [11 empty] | 13265 | 2076.3732 | 2065.9913 | 2055.6614 | 2045.3831 | 2035.1562 | 2024.9804 | 2014.8555 | 0.92643 | [6 empty] | 68.4286 | 1621.2857 | 3.677% | -113.8364 | 2781.4182 | -7.732% | 93810.9388 | 392054.8776 | 25417.4694 | 12769 | 31887.7551 | 1669.3061 | 8151.5102 | 59.7107 | 4609.1755 | 66077.0393 | 50078.3021 | 123635.3458 | 69936.2066 | 413074.9755 | 33442.4344 | 85827.6922 | [7 empty] | 18.3% | 3.3% | 18.03% | 15% | 22%
25 | 56889 | PPL Merck | 2010 | 2009 | IPP Non-CHP | c-Si | Unknown | Fixed | 2 | NJ | 40.727 | -74.378 | 1.8 | 1.7 | 1424.475 | Newark | 12.7 | 34.7365 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 2051.244 | 1623 | 1483 | 1628 | 1563 | 671 | 1591 | 1659 | 1458 | 1369 | 1500 | 1459 | 1259 | 1128 | 691 | 0 | [8 empty] | 15 |  | 25 | 0.79123 | 0.72661 | 0.80166 | 0.77352 | 0.33374 | 0.79531 | 0.83347 | 0.73617 | 0.69471 | 0.76501 | 0.74784 | 0.64857 | 0.584 | 0.35955 | 0 | [8 empty] | 25 | 29714.7436 | 19082 | 0.64217 | 92 | Fixed | -4.912% | -64.0607 | 1784.619 | [18 empty] | 1.0588 | 1 | [11 empty] | 10218 | 2051.244 | 2040.9878 | 2030.7828 | 2020.6289 | 2010.5258 | 2000.4732 | 1990.4708 | 0.72237 |  |  | 0.64217 | -4.912% |  | 0.72237 | -22.6071 | 1550.1429 | -1.537% | -161 | 2940.2222 | -13.77% | 9113.4298 | 480.8622 | 21222.2462 | 10667.9388 | 586920.1543 | 31152.25 | 71346.2258 | 37722.2716 | 14938.2716 | 28824.4938 | 83971.1605 | 62889.4938 | 78836.1605 | 22.8272 | 275858.3827 | [8 empty] | 23.27% | 2.5% | 10.75% | 22.14% | 11.29%
26 | 57204 | PSEG Hackettstown | 2010 | 2009 | IPP Non-CHP | c-Si | Other utility | Fixed | 20 | NJ | 40.8606 | -74.8229 | 2.2 | 2 | 1607.1 | Allentown | 10.7 | 34.094 | C | 1419 | 698 | 0.494 | 0.4919 | 0% | 1 | 2828.496 | 2744 | 2412 | 2740 | 2656 | 2510 | 2471 | 2628 | 2408 | 2167 | 2391 | 2382 | 2241 | 2395 | 2285 | 1761 | [8 empty] | 15 |  | 26 | 0.97013 | 0.85704 | 0.97847 | 0.95324 | 0.90537 | 0.89578 | 0.95748 | 0.88174 | 0.79748 | 0.88433 | 0.88543 | 0.83721 | 0.89923 | 0.86224 | 0.66785 | [8 empty] | 26 | 40974.1764 | 36191 | 0.88326 | 47 | Fixed | -1.765% | -42.975 | 2756.5333 | [18 empty] | 1.1 | 1 | [11 empty] | 18161 | 2828.496 | 2814.3535 | 2800.2818 | 2786.2803 | 2772.3489 | 2758.4872 | 2744.6948 | 0.9311 |  |  | 0.88326 | -1.765% |  | 0.9311 | -16.4286 | 2660.1429 | -0.6312% | -58.85 | 2942.6833 | -2.564% | 10057.2245 | 46347.9388 | 16677.8776 | 3791.0408 | 4624 | 8203.1837 | 6865.3061 | 4081.0803 | 60532.4011 | 1355.4669 | 7511.1111 | 20.4003 | 47248.2678 | 27627.9803 | 89361.1378 | [8 empty] | 6.188% | 2.9% | 46.87% | 4.527% | 64.06%
27 | 57141 | RV CSU | 2010 | 2009 | Commercial Non-CHP | c-Si | MMA | Tracker | 0 | CO | 40.591 | -105.146 | 2 | 1.9 | 2337.6 | Boulder | 10.2 | 39.024 | C | 1689 | 562 | 0.583 | 0.33274 | 0% | 1 | 3553.152 | 3460 | 3422 | 3520 | 3389 | 2930 | 2991 | 4610 | 3350 | 3391 | 3007 | 2998 | 3013 | 2290 | 2514 | 1757 | [8 empty] | 15 |  | 27 | 0.97378 | 0.96793 | 1.0007 | 0.96825 | 0.84132 | 0.86315 | 1.15 | 0.97649 | 0.99341 | 0.88534 | 0.88713 | 0.89605 | 0.68445 | 0.75518 | 0.53044 | [8 empty] | 27 | 51471.6927 | 46642 | 0.90617 | 37 | Tracker | -2.943% | -92.8786 | 3852.4952 | [18 empty] | 1.0526 | 1 | [11 empty] | 24322 | 3553.152 | 3535.3862 | 3517.7093 | 3500.1208 | 3482.6202 | 3465.2071 | 4008.6957 | 0.97044 |  |  | 0.90617 | -2.943% |  | 0.97044 | 71.3571 | 3189.1429 | 2.075% | -268.6 | 5946.8222 | -8.977% | 39800.25 | 8125.7347 | 13638.9031 | 7322.4694 | 379368.0051 | 392233.7959 | 848898.9847 | 200723.9116 | 19160.7116 | 64425.7205 | 33.3827 | 83739.4983 | 27232.3338 | 107307.2005 | 25863.7872 | [8 empty] | 12.37% | 5.1% | 41.24% | 14.14% | 36.07%
28 | 56939 | Solar Blythe (NRG) | 2010 | 2009 | IPP Non-CHP | CdSCdTe | NRG | Fixed | 24 | CA | 33.592 | -114.744 | 26.4 | 21 | 2374.125 | Daggett | 19.8 | 48.8955 | M | 2138 | 489 | 0.696 | 0.22872 | 1.378% | 0.83712 | 50141.52 | 49855 | 51275 | 47708 | 47624 | 46740 | 45908 | 45470 | 44008 | 42291 | 43320 | 41561 | 41258 | 42013 | 40522 | 41770 | [8 empty] | 15 |  | 28 | 0.99429 | 1.0277 | 0.96105 | 0.96418 | 0.95104 | 0.93881 | 0.93452 | 0.90902 | 0.87794 | 0.90382 | 0.87148 | 0.86947 | 0.88983 | 0.86257 | 0.8936 | [8 empty] | 28 | 726360.3997 | 671323 | 0.92423 | 30 | Fixed | -1.575% | -710.5143 | 50438.981 | [18 empty] | 1.2571 | 1 | [11 empty] | 334580 | 50141.52 | 49890.8124 | 49641.3583 | 49393.1515 | 49146.1858 | 48900.4549 | 48655.9526 | 0.96764 | [6 empty] | -887.75 | 51348.1429 | -1.84% | -464.6 | 47578.7111 | -1.094% | 366500.5115 | 2898019.8418 | 954319.6543 | 29978.449 | 28693.9401 | 12914.699 | 112968.0115 | 21341.9635 | 1223924.2746 | 149992.6835 | 822850.5679 | 555786.8168 | 224760.2746 | 305047.5635 | 1346270.3057 | [8 empty] | 1.736% | 2.2% | 126.7% | 1.659% | 132.6%
29 | 56996 | Solar PV #02 (SCE) | 2010 | 2009 | Electric Utility | CdSCdTe | Other utility | Fixed | 2 | CA | 33.99 | -117.7 | 1.2 | 1 | 1881.0375 | Chino (Meteonorm) | 17.7 | 43.1303 | M | 1849 | 627 | 0.596 | 0.3391 | 0% | 1 | 1805.796 | 1421 | 1312 | 887 | 951 | 791 | 703 | 899 | 580 | 365 | 661 | 722 | 1190 | 710 | 0 | 0 | [8 empty] | 15 |  | 29 | 0.78691 | 0.7302 | 0.49615 | 0.53462 | 0.44691 | 0.39918 | 0.51304 | 0.33266 | 0.2104 | 0.38293 | 0.42038 | 0.69634 | 0.41755 | 0 | 0 | [8 empty] | 29 | 26159.1333 | 11192 | 0.42784 | 98 | Fixed | -8.512% | -66.3321 | 1276.7905 | [18 empty] | 1.2 | 1 | [11 empty] | 6964 | 1805.796 | 1796.767 | 1787.7832 | 1778.8443 | 1769.95 | 1761.1003 | 1752.2948 | 0.55924 | [6 empty] | -102.8571 | 1406.2857 | -9.831% | -68.6167 | 1324.45 | -12.05% | 13823.0408 | 12416.3265 | 44400.5102 | 1923.449 | 10201 | 7420.5918 | 45247.3673 | 38226.7669 | 116895.61 | 516.0469 | 23205.4444 | 474652.1025 | 77043.2544 | 132362.5669 | 87143.04 | [8 empty] | 36.05% | 2.1% | 5.825% | 13.98% | 15.02%
30 | 57010 | SunE Anheuser | 2009 | 2009 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | CA | 38.232 | -122.093 | 1.2 | 1 | 2483.7 | Sacramento | 16 | 45.91 | M | 1793 | 572 | 0.608 | 0.31902 | 4.302% | 0.57409 | 2265.1344 | 2207 | 2073 | 2176 | 2143 | 2201 | 2091 | 2055 | 2642 | 1628 | 1699 | 1582 | 1380 | 1700 | 1665 | 747 | 1187 | [7 empty] | 16 |  | 30 | 0.97434 | 0.91978 | 0.97033 | 0.96042 | 0.99137 | 0.94655 | 0.93493 | 1.15 | 0.74813 | 0.78468 | 0.73431 | 0.64377 | 0.79704 | 0.78455 | 0.35376 | 0.56495 | [7 empty] | 30 | 34914.2725 | 29176 | 0.83565 | 60 | Tracker | -4.148% | -77.2353 | 2480 | [18 empty] | 1.2 | 0 | [11 empty] | 14946 | 2265.1344 | 2253.8087 | 2242.5397 | 2231.327 | 2220.1704 | 2209.0695 | 2198.0242 | 0.95685 | [6 empty] | -14.1071 | 2191.5714 | -0.6585% | -127.8242 | 3098.4788 | -7.849% | 872.3584 | 8164.4133 | 715.5625 | 61.7347 | 6394.287 | 253.7194 | 1430.4605 | 320486.3648 | 102438.7916 | 14698.2559 | 12190.8365 | 34072.685 | 69293.3831 | 126779.1552 | 188455.9648 | 17878.121 | [7 empty] | 13.04% | 3.3% | 25.31% | 2.368% | 139.4%
31 | 57007 | SunE Ironwood | 2009 | 2009 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | CA | 33.5634 | -114.9192 | 1.2 | 1 | 3068.1 | Daggett | 19.8 | 54.054 | H | 2138 | 489 | 0.696 | 0.22872 | 8.307% | 0.34244 | 2798.1072 | 2578 | 2615 | 2678 | 2448 | 2266 | 2292 | 2112 | 3722 | 1627 | 2215 | 1799 | 2004 | 1711 | 425 | 1252 | 996 | [7 empty] | 16 |  | 31 | 0.92134 | 0.93926 | 0.96672 | 0.88813 | 0.82623 | 0.83991 | 0.77784 | 1.15 | 0.60526 | 0.82814 | 0.67598 | 0.7568 | 0.64939 | 0.16212 | 0.47997 | 0.38375 | [7 empty] | 31 | 43129.3954 | 32740 | 0.75911 | 76 | Tracker | -5.517% | -116.1029 | 3033.125 | [18 empty] | 1.2 | 0 | [11 empty] | 16989 | 2798.1072 | 2784.1167 | 2770.1961 | 2756.3451 | 2742.5634 | 2728.8506 | 2715.2063 | 0.88047 | 0.75911 | -5.517% |  |  | 0.88047 |  | -87.7143 | 2777.8571 | -3.55% | -210.0061 | 4201.3697 | -11.76% | 12576.0204 | 158.0408 | 26662.2245 | 441 | 5370.7959 | 1634.4694 | 2689.1633 | 1441629.5517 | 468287.2266 | 12925.6228 | 8519.8494 | 104137.2458 | 57460.4483 | 699372.3478 | 40289.005 | 23940.5289 | [7 empty] | 20.83% | 2.8% | 13.44% | 3.466% | 80.79%
32 | 56938 | SunE LV Sutton | 2009 | 2009 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | NC | 34.2867 | -77.9814 | 1.2 | 1 | 2154.975 | Wilmington NC | 12.3 | 39.7665 | C | 1632.6 | 720 | 0.528 | 0.44101 | 4.387% | 0.5678 | 1965.3372 | 1466 | 1999 | 1955 | 1865 | 1683 | 1920 | 1823 | 1216 | 1519 | 936 | 1736 | 1452 | 1330 | 334 | 1153 | 1122 | [7 empty] | 16 |  | 32 | 0.74593 | 1.0222 | 1.0048 | 0.96332 | 0.87368 | 1.0017 | 0.9559 | 0.64082 | 0.80452 | 0.49823 | 0.92871 | 0.78068 | 0.71868 | 0.18139 | 0.62932 | 0.61547 | [7 empty] | 32 | 30293.2658 | 23509 | 0.77605 | 73 | Tracker | -4.28% | -64.2632 | 2015.55 | [18 empty] | 1.2 | 0 | [11 empty] | 12711 | 1965.3372 | 1955.5105 | 1945.733 | 1936.0043 | 1926.3243 | 1916.6927 | 1907.1092 | 0.93789 |  |  | 0.77605 | -4.28% |  | 0.93789 | 22.8929 | 1724.2857 | 1.269% | -71.3758 | 2082.9212 | -5.655% | 79061.389 | 52408.2908 | 26255.5727 | 2415.0204 | 24258.0625 | 3405.5561 | 3786.6441 | 87565.7769 | 6156.0667 | 187630.7359 | 192029.8632 | 50889.8911 | 30612.274 | 561991.0243 | 19800.7539 | 32793.9174 | [7 empty] | 19.85% | 3.2% | 16.12% | 9.111% | 35.12%
33 | 57008 | SunE Oxnard | 2010 | 2009 | IPP Non-CHP | CdSCdTe | SunEdison | Fixed | 20 | CA | 34.2093 | -119.1345 | 1.2 | 1 | 2008.875 | Los Angeles | 17.2 | 43.5805 | M | 1818 | 676 | 0.586 | 0.37184 | 0.373% | 0.95302 | 1928.52 | 1762 | 1726 | 1710 | 1838 | 1956 | 1923 | 1839 | 1653 | 1629 | 1691 | 1775 | 1760 | 2684 | 1475 | 1634 | [8 empty] | 15 |  | 33 | 0.91365 | 0.89948 | 0.89562 | 0.9675 | 1.0348 | 1.0224 | 0.9827 | 0.88774 | 0.87925 | 0.9173 | 0.96771 | 0.96435 | 1.15 | 0.81633 | 0.90888 | [8 empty] | 33 | 27936.9385 | 27055 | 0.96843 | 18 | Fixed | 0.1861% | 3.3536 | 1776.8381 | [18 empty] | 1.2 | 1 | [11 empty] | 12754 | 1928.52 | 1918.8774 | 1909.283 | 1899.7366 | 1890.2379 | 1880.7867 | 1871.3828 | 0.95903 | [6 empty] | 31.1071 | 1697.5714 | 1.722% | 13.75 | 1642.0833 | 0.7667% | 1110.3176 | 1141.4745 | 6543.6543 | 256 | 10586.9401 | 1504.3316 | 5824.9605 | 9817.5069 | 18723.3611 | 7847.0069 | 336.1111 | 2216.8403 | 745056.6944 | 129300.1736 | 45938.7778 | [8 empty] | 14.22% | 2.6% | 18.29% | 3.407% | 76.32%
34 | 57004 | SunE Moreno Valley | 2009 | 2007 | IPP Non-CHP | c-Si | SunEdison | Fixed | 20 | CA | 33.8659 | -117.2215 | 1.2 | 1 | 2158.6275 | Moreno Valley (Meteonorm) | 17.3 | 44.7936 | M | 1932 | 579 | 0.622 | 0.29969 | 0% | 1 | 2072.2824 | 2008 | 1968 | 1953 | 1951 | 1855 | 1839 | 1780 | 941 | 1191 | 1681 | 887 | 1459 | 1333 | 1074 | 1259 | 900 | [7 empty] | 16 |  | 34 | 0.96898 | 0.95445 | 0.95193 | 0.95574 | 0.91328 | 0.90995 | 0.88518 | 0.4703 | 0.59824 | 0.84862 | 0.45003 | 0.74396 | 0.68313 | 0.55317 | 0.65171 | 0.46822 | [7 empty] | 34 | 31941.6951 | 24079 | 0.75384 | 77 | Fixed | -4.643% | -71.5397 | 2113.025 | [18 empty] | 1.2 | 2 | [11 empty] | 13354 | 2072.2824 | 2061.921 | 2051.6114 | 2041.3533 | 2031.1466 | 2020.9908 | 2010.8859 | 0.93449 | [6 empty] | -37.1429 | 2056.2857 | -1.928% | -40.9152 | 1721.0242 | -3.272% | 124.1633 | 196 | 66.3061 | 1873.6531 | 242.4694 | 31.0408 | 265.2245 | 204940.0336 | 26175.3177 | 136254.9435 | 147423.42 | 52421.5715 | 20699.3617 | 5507.4389 | 23013.8094 | 27682.9094 | [7 empty] | 13.36% | 2.4% | 17.96% | 1.048% | 229%
35 | 57012 | SunE Apple Valley | 2010 | 2009 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | CA | 34.5975 | -117.2 | 1.2 | 1 | 3068.1 | Daggett | 19.8 | 54.054 | H | 2138 | 489 | 0.696 | 0.22872 | 8.307% | 0.34244 | 2798.1072 | 2509 | 2631 | 2445 | 2619 | 2588 | 2402 | 2398 | 1628 | 2330 | 2236 | 2305 | 1809 | 2168 | 969 | 716 | [8 empty] | 15 |  | 35 | 0.89668 | 0.945 | 0.88261 | 0.95017 | 0.94364 | 0.88022 | 0.88317 | 0.6026 | 0.86678 | 0.83599 | 0.86612 | 0.68316 | 0.82284 | 0.36962 | 0.27449 | [8 empty] | 35 | 40533.958 | 31753 | 0.78337 | 70 | Tracker | -4.679% | -101.4179 | 2928.2095 | [18 empty] | 1.2 | 1 | [11 empty] | 17592 | 2798.1072 | 2784.1167 | 2770.1961 | 2756.3451 | 2742.5634 | 2728.8506 | 2715.2063 | 0.91172 | 0.78337 | -4.679% |  |  | 0.91172 |  | -23.1429 | 2605.7143 | -0.9167% | -157.6 | 3573.4889 | -8.566% | 5412.7551 | 5122.4694 | 8333.0816 | 11205.7347 | 9604 | 4206.449 | 2089.7959 | 468798.8746 | 30593.8968 | 56887.5501 | 216328.3457 | 16055.7057 | 413849.1857 | 158474.7635 | 243531.2835 | [8 empty] | 15.67% | 2.8% | 17.87% | 3.225% | 86.83%
36 | 57041 | PG&E Vaca-Dixon | 2010 | 2009 | Electric Utility | c-Si | PG&E | Fixed | 30 | CA | 38.4106 | -121.9264 | 2.6 | 2 | 2008.875 | Sacramento | 16 | 42.3805 | M | 1793 | 572 | 0.608 | 0.31902 | 0.6352% | 0.92132 | 4178.46 | 4189 | 4345 | 4221 | 4707 | 4056 | 4425 | 4028 | 3434 | 4069 | 3074 | 3579 | 3093 | 3941 | 3714 | 3242 | [8 empty] | 15 |  | 36 | 1.0025 | 1.0451 | 1.0204 | 1.1436 | 0.99035 | 1.0859 | 0.99342 | 0.85118 | 1.0136 | 0.76963 | 0.90056 | 0.78219 | 1.0016 | 0.94869 | 0.83229 | [8 empty] | 36 | 60530.0333 | 58117 | 0.96013 | 22 | Fixed | -2.04% | -79.8679 | 4513.4095 | [18 empty] | 1.3 | 1 | [11 empty] | 29971 | 4178.46 | 4157.5677 | 4136.7799 | 4116.096 | 4095.5155 | 4075.0379 | 4054.6627 | 1.0401 | [6 empty] | -17.4286 | 4351.2857 | -0.4062% | -42.35 | 4040.7389 | -1.185% | 20983.5918 | 816.3265 | 6084 | 180989.4694 | 43323.449 | 31785.7959 | 40515.9388 | 71791.2482 | 167617.4579 | 295108.4904 | 16.9012 | 193194.4348 | 203230.6579 | 70841.7371 | 26728.6168 | [8 empty] | 7.752% | 3.2% | 41.28% | 5.029% | 63.63%
37 | 56922 | WWRF Rifle SunE | 2010 | 2009 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | CO | 39.523 | -107.813 | 2.2 | 1.5 | 2556.75 | Grand Junction | 11.7 | 42.153 | M | 1823 | 575 | 0.622 | 0.31541 | 11.83% | 0.21733 | 4274.886 | 3115 | 2973 | 3174 | 2922 | 2973 | 0 | 2981 | 2809 | 2960 | 2852 | 2744 | 1991 | 2084 | 1002 | 1699 | [8 empty] | 15 |  | 37 | 0.72867 | 0.69895 | 0.74996 | 0.69388 | 0.70954 | 0 | 0.71862 | 0.68056 | 0.72075 | 0.69794 | 0.67488 | 0.49214 | 0.51772 | 0.25017 | 0.42633 | [8 empty] | 37 | 61926.8802 | 36279 | 0.58584 | 96 | Tracker | -3.755% | -92.5571 | 3159.0571 | [18 empty] | 1.4667 | 1 | [11 empty] | 18138 | 4274.886 | 4253.5116 | 4232.244 | 4211.0828 | 4190.0274 | 4274.886 | 4148.2319 | 0.61308 | [6 empty] | -233.8929 | 3526.7143 | -8.637% | -219.3667 | 4759.9222 | -9.347% | 31620.4605 | 7383.7194 | 121776.0727 | 109466.449 | 379148.0625 | 4508645.5561 | 1191450.2156 | 38411.6446 | 30407.6094 | 81649.8875 | 157697.2346 | 18638.3172 | 30921.2686 | 471678.9779 | 52705.956 | [8 empty] | 28.71% | 4.7% | 16.37% | 36.76% | 12.79%
38 | 57006 | Woodland Walgreens SunE | 2009 | 2009 | IPP Non-CHP | c-Si | SunEdison | Fixed | 15 | CA | 38.675 | -121.713 | 1.2 | 0.9 | 1858.2094 | Sacramento | 16 | 41.2606 | M | 1793 | 572 | 0.608 | 0.31902 | 0% | 1 | 1783.881 | 1800 | 1681 | 1733 | 1656 | 1544 | 1586 | 1470 | 460 | 660 | 832 | 1569 | 1346 | 1187 | 1011 | 775 | 908 | [7 empty] | 16 |  | 38 | 1.009 | 0.94706 | 0.98127 | 0.94238 | 0.88306 | 0.91164 | 0.84921 | 0.26707 | 0.38512 | 0.48792 | 0.92475 | 0.79731 | 0.70666 | 0.6049 | 0.46603 | 0.54875 | [7 empty] | 38 | 27496.3407 | 20218 | 0.7353 | 83 | Fixed | -4.605% | -59.5676 | 1769.95 | [18 empty] | 1.3333 | 0 | [11 empty] | 11470 | 1783.881 | 1774.9616 | 1766.0868 | 1757.2564 | 1748.4701 | 1739.7277 | 1731.0291 | 0.93241 | [6 empty] | -48.8929 | 1834.1429 | -2.94% | -1.5515 | 1039.6424 | -0.1518% | 217.5625 | 3064.4133 | 2073.5013 | 303.7551 | 2086.5319 | 2044.3316 | 479.2972 | 321750.2167 | 133720.9759 | 36912.8889 | 298579.4527 | 105609.243 | 28065.3871 | 47.9032 | 58259.3306 | 11410.124 | [7 empty] | 19.83% | 2.8% | 14.12% | 2.338% | 119.8%
39 | 54569 | Bayville Central | 2010 | 2007 | Commercial CHP | c-Si | Unknown | Fixed | 10 | NJ | 39.909 | -74.178 | 0.28 | 0.5 | 1570.575 | Atlantic City | 11.7 | 34.8225 | C | 1486 | 672 | 0.509 | 0.45222 | 0% | 1 | 351.8088 | 217 | 229 | 247 | 240 | 249 | 278 | 294 | 233 | 217 | 91 | 96 | 239 | 218 | 185 | 173 | [8 empty] | 15 |  | 39 | 0.61681 | 0.65419 | 0.70916 | 0.69252 | 0.7221 | 0.81026 | 0.8612 | 0.68594 | 0.64205 | 0.2706 | 0.2869 | 0.71786 | 0.65807 | 0.56126 | 0.52749 | [8 empty] | 39 | 5096.3748 | 3206 | 0.62907 | 93 | Fixed | -2.689% | -5.825 | 260.3333 | [18 empty] | 0.56 | 3 | [11 empty] | 1754 | 351.8088 | 350.0498 | 348.2995 | 346.558 | 344.8252 | 343.1011 | 341.3856 | 0.72299 |  |  | 0.62907 | -2.689% |  | 0.72299 | 11.8214 | 203.2857 | 4.832% | -7.9667 | 281.6333 | -4.107% | 3.5829 | 4.2908 | 68.0625 | 111.7551 | 179.3686 | 14.3316 | 63.4298 | 228.01 | 49.9378 | 12313.6011 | 9604 | 2805.4678 | 1594.6711 | 222.01 | 118.0844 | [8 empty] | 19.99% | 2.75% | 13.76% | 3.181% | 86.44%
40 | 57197 | Blue Wing | 2011 | 2010 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 20 | TX | 29.304 | -98.4 | 16.7 | 13.9 | 1957.74 | San Antonio | 20.3 | 46.3004 | M | 1815 | 758 | 0.56 | 0.41763 | 1.295% | 0.84616 | 26155.4064 | 28639 | 25193 | 23688 | 23141 | 21969 | 23182 | 22594 | 21795 | 21717 | 20442 | 19846 | 21319 | 17787 | 19079 | [9 empty] | 14 |  | 40 | 1.095 | 0.96804 | 0.91479 | 0.89816 | 0.85695 | 0.90881 | 0.89021 | 0.86305 | 0.86428 | 0.81763 | 0.79778 | 0.86129 | 0.72221 | 0.77856 | [9 empty] | 40 | 354509.7537 | 310391 | 0.87555 | 51 | Fixed | -2.573% | -577.9363 | 26505.3077 | [18 empty] | 1.2014 | 1 | [11 empty] | 168406 | 26155.4064 | 26024.6294 | 25894.5062 | 25765.0337 | 25636.2085 | 25508.0275 | 25380.4873 | 0.9337 | [6 empty] | -852.7143 | 27468.8571 | -3.483% | -552.7976 | 26376.75 | -2.687% | 4091951.0204 | 325388.7551 | 1495030.2245 | 840889 | 1528402.3673 | 687951.7551 | 1197148.5918 | 25398.4933 | 99495.1837 | 165464.9321 | 202478.572 | 2483213.1747 | 1969478.0975 | 194848.6736 | [9 empty] | 4.716% | 2.4% | 50.89% | 5.009% | 47.91%
41 | 57205 | Copper Mtn 48 (FS) | 2011 | 2010 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 24 | NV | 35.7814 | -114.993 | 60.5 | 48 | 2337.6 | Las Vegas | 19.5 | 48.324 | M | 2078 | 550 | 0.684 | 0.26468 | 2.179% | 0.75499 | 113139.84 | 108044 | 106378 | 105251 | 103456 | 101936 | 98291 | 101204 | 100205 | 97974 | 100294 | 94345 | 98100 | 93271 | 94346 | [9 empty] | 14 |  | 41 | 0.95496 | 0.94496 | 0.93965 | 0.92826 | 0.91922 | 0.89081 | 0.92181 | 0.9173 | 0.90139 | 0.92737 | 0.87674 | 0.91622 | 0.8755 | 0.89004 | [9 empty] | 41 | 1533494.6892 | 1403095 | 0.91497 | 34 | Fixed | -1.005% | -1012.1912 | 107812.5055 | [18 empty] | 1.2604 | 1 | [11 empty] | 724560 | 113139.84 | 112574.1408 | 112011.2701 | 111451.2137 | 110893.9577 | 110339.4879 | 109787.7904 | 0.92869 | [6 empty] | -1428.8929 | 109224.1429 | -1.371% | -1050.5595 | 108498.25 | -1.078% | 61876.5625 | 135.5561 | 98304.6441 | 2763.7551 | 20643.5319 | 5568588.6173 | 3928748.7258 | 12371.2654 | 1143219.1888 | 5296189.9049 | 6744903.6757 | 4877314.5013 | 2464825.2387 | 308672.8403 | [9 empty] | 1.473% | 3% | 203.6% | 1.136% | 264%
42 | 56768 | CalRenew-1 | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 20 | CA | 36.7575 | -120.366 | 6.3 | 5 | 2081.925 | Fresno | 17.4 | 44.3235 | M | 1910 | 578 | 0.634 | 0.30262 | 0.2128% | 0.97292 | 10492.902 | 9887 | 10478 | 10786 | 10420 | 10185 | 9358 | 9825 | 9855 | 8964 | 9180 | 5268 | 8479 | 6326 | 1334 | [9 empty] | 14 |  | 42 | 0.94226 | 1.0036 | 1.0383 | 1.0081 | 0.99031 | 0.91448 | 0.96494 | 0.97275 | 0.88925 | 0.91525 | 0.52786 | 0.85388 | 0.64026 | 0.13569 | [9 empty] | 42 | 142220.5431 | 120345 | 0.84619 | 58 | Fixed | -5.468% | -483.2198 | 12220.2198 | [18 empty] | 1.26 | 1 | [11 empty] | 70939 | 10492.902 | 10440.4375 | 10388.2353 | 10336.2941 | 10284.6127 | 10233.1896 | 10182.0236 | 0.98039 | [6 empty] | -108.1071 | 10566.5714 | -1.061% | -981.5357 | 17710 | -13.26% | 326571.4298 | 16292.699 | 295664.0625 | 81714.3061 | 25269.6441 | 313520.0051 | 230.389 | 7.3673 | 7712.6033 | 1652142.9847 | 2706377.5115 | 6489392.3265 | 1893277.7156 | 6940590.25 | [9 empty] | 14.16% | 3.6% | 25.42% | 3.839% | 93.79%
43 | 57509 | Carson | 2010 | 2007 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | CO | 38.7228 | -104.7817 | 2 | 2 | 2008.875 | Colorado Springs | 9.2 | 35.5805 | C | 1726.5 | 544.7 | 0.587 | 0.31549 | 0% | 1 | 3214.2 | 3037 | 3126 | 3112 | 2501 | 2110 | 2411 | 2695 | 2189 | 1645 | 0 | 2287 | 3326 | 2962 | 3012 | 3149 | [8 empty] | 15 |  | 43 | 0.94487 | 0.97745 | 0.97796 | 0.7899 | 0.66976 | 0.76915 | 0.86407 | 0.70536 | 0.53273 | 0 | 0.7481 | 1.0934 | 0.97867 | 1.0002 | 1.0509 | [8 empty] | 43 | 46561.5641 | 37562 | 0.80672 | 66 | Fixed | -0.3831% | -9.6107 | 2581.019 | [18 empty] | 1 | 3 | [11 empty] | 18992 | 3214.2 | 3198.129 | 3182.1384 | 3166.2277 | 3150.3965 | 3134.6445 | 3118.9713 | 0.85686 |  |  | 0.80672 | -0.3831% |  | 0.85686 | -123.5 | 3207.1429 | -4.451% | 170.75 | 484.5278 | 7.227% | 2175.5561 | 27508.5918 | 75821.5561 | 45004.5918 | 230057.2704 | 3040.7347 | 124155.5561 | 114563.4452 | 141584.966 | 4804985.7785 | 5742.2716 | 628012.223 | 66420.7438 | 18761.3897 | 10654.8272 | [8 empty] | 25.88% | 3.1% | 11.98% | 9.927% | 31.23%
44 | 57243 | Cimarron | 2011 | 2010 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 25 | NM | 36.468 | -104.636 | 37.4 | 30.6 | 2228.025 | Alamosa | 5.1 | 33.1095 | C | 1926 | 518 | 0.644 | 0.26895 | 0.1004% | 0.98713 | 66662.508 | 67978 | 69919 | 66592 | 62443 | 60785 | 63694 | 60971 | 63266 | 61710 | 62525 | 63263 | 60678 | 57027 | 44625 | [9 empty] | 14 |  | 44 | 1.0197 | 1.0541 | 1.009 | 0.9509 | 0.9303 | 0.97972 | 0.94255 | 0.98294 | 0.96358 | 0.98122 | 0.99779 | 0.96182 | 0.90849 | 0.71449 | [9 empty] | 44 | 903542.0413 | 865476 | 0.95787 | 23 | Fixed | -1.719% | -1072.1846 | 69861.0989 | [18 empty] | 1.2222 | 1 | [11 empty] | 452382 | 66662.508 | 66329.1955 | 65997.5495 | 65667.5617 | 65339.2239 | 65012.5278 | 64687.4652 | 0.98409 |  |  | 0.95787 | -1.719% |  | 0.98409 | -1402.7857 | 70237.1429 | -2.147% | -1761.6071 | 77755 | -2.973% | 733347.5561 | 6187300.898 | 317210.3316 | 4765489 | 5944888.9031 | 3510269.898 | 306204.1276 | 156929.1633 | 36303.8584 | 5693336.8622 | 23869855.1033 | 16502165.2245 | 4721463.3686 | 71698556.25 | [9 empty] | 5.196% | 2.5% | 48.12% | 2.728% | 91.63%
45 | 57216 | Crayola | 2013 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | PA | 40.7605 | -75.238 | 3.1 | 2.8 | 1607.1 | Allentown | 10.7 | 34.094 | C | 1419 | 698 | 0.494 | 0.4919 | 0% | 1 | 3985.608 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2515; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2989; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3105; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 4401; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2655; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2560; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 2653; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 2666; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 2505; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 2794; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 2709; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 2628; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 2340; Median age 14: 13 |  | 45 | 0.63102 | 0.75372 | 0.7869 | 1.121 | 0.67964 | 0.65861 | 0.68597 | 0.69279 | 0.65423 | 0.73337 | 0.71463 | 0.69675 | 0.62351 | [10 empty] | 45 | 50286.6609 | 36520 | 0.72624 | 84 | Fixed | -1.832% | -51.9451 | 3172.8462 | [18 empty] | 1.1071 | 3 | [11 empty] | 20878 | 3985.608 | 3965.68 | 3945.8516 | 3926.1223 | 3906.4917 | 3886.9592 | 3867.5244 | 0.75964 |  |  | 0.72624 | -1.832% |  | 0.75964 | -31.9286 | 3110.2857 | -1.065% | -28.9643 | 2903.2143 | -1.108% | 317371.2704 | 3298.0408 | 8190.25 | 2011939.6122 | 87404.699 | 128675.9388 | 54655.7602 | 30.25 | 18916.0727 | 32554.4694 | 15473.5829 | 5235.5561 | 34848.889 | [10 empty] | 16.28% | 2.9% | 17.81% | 20.48% | 14.16%
46 | 57334 | Duke Egy 10240 | 2012 | 2010 | Electric Utility | c-Si | Duke | Fixed | 5 | NC | 35.246 | -80.9967 | 2.2 | 1.9 | 1652.7563 | Charlotte | 15.6 | 39.3334 | C | 1635 | 689 | 0.534 | 0.42141 | 0% | 1 | 2908.851 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2558; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2847; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2713; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2712; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2477; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2541; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1978; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 1661; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 2010; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 2003; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 2067; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 1447; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 1534; Median age 14: 13 |  | 46 | 0.87939 | 0.98366 | 0.94207 | 0.94645 | 0.86878 | 0.89571 | 0.70076 | 0.59141 | 0.71927 | 0.72036 | 0.74712 | 0.52565 | 0.56005 | [10 empty] | 46 | 36701.1517 | 28548 | 0.77785 | 71 | Fixed | -4.803% | -108.0714 | 2952.5 | [18 empty] | 1.1579 | 2 | [11 empty] | 17826 | 2908.851 | 2894.3067 | 2879.8352 | 2865.436 | 2851.1089 | 2836.8533 | 2822.669 | 0.88868 |  |  | 0.77785 | -4.803% |  | 0.88868 | -92.4286 | 2916.2857 | -3.565% | -60.8214 | 2422.5 | -3.352% | 70680.0204 | 13356.7551 | 5476 | 27366.6122 | 522.449 | 32143.3673 | 84847.3673 | 75585.7194 | 18196.0829 | 35613.0816 | 98304.6441 | 60340.4133 | 9569.0319 | [10 empty] | 9.212% | 2.5% | 27.14% | 7.186% | 34.79%
47 | 57336 | Duke Egy 1725 | 2010 | 2010 | Electric Utility | c-Si | Duke | Fixed | 11 | NC | 35.326 | -80.997 | 1.2 | 1 | 1698.4125 | Charlotte | 15.6 | 39.6728 | C | 1635 | 689 | 0.534 | 0.42141 | 0% | 1 | 1630.476 | 1545 | 380 | 468 | 1543 | 1545 | 1545 | 1666 | 1546 | 1380 | 1286 | 1317 | 814 | 975 | 796 | 902 | [8 empty] | 15 |  | 47 | 0.94758 | 0.23423 | 0.28992 | 0.96069 | 0.96677 | 0.97162 | 1.053 | 0.98205 | 0.88101 | 0.82512 | 0.84926 | 0.52754 | 0.63506 | 0.52107 | 0.59343 | [8 empty] | 47 | 23619.4116 | 17708 | 0.74972 | 78 | Fixed | -1.165% | -13.8357 | 1291.219 | [18 empty] | 1.2 | 0 | [11 empty] | 8692 | 1630.476 | 1622.3236 | 1614.212 | 1606.1409 | 1598.1102 | 1590.1197 | 1582.1691 | 0.77307 |  |  | 0.74972 | -1.165% |  | 0.77307 | 134.6429 | 703.1429 | 11.46% | -109.8 | 2394.6889 | -9.251% | 500152.0459 | 350971.6122 | 408412.2908 | 90773.0816 | 28440.4133 | 1156 | 414.4133 | 882.7501 | 701.6612 | 114.2523 | 16928.9012 | 69215.7635 | 59.4612 | 3780.8835 | 23811.919 | [8 empty] | 26.75% | 2.6% | 9.72% | 35.76% | 7.27%
48 | 57335 | Duke Egy 657 | 2013 | 2010 | Electric Utility | c-Si | Duke | Fixed | 15 | NC | 36.107 | -79.97 | 1.5 | 1.3 | 1737.6769 | Greensboro | 14.3 | 38.6646 | C | 1615 | 683 | 0.532 | 0.42291 | 0% | 1 | 2085.2123 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2120; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2069; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1705; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1895; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2066; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2000; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1844; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 1510; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 1351; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 855; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 810; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 428; Median age 14: 12 |  | 48 | 1.0167 | 0.99721 | 0.8259 | 0.92255 | 1.0109 | 0.98348 | 0.91132 | 0.75001 | 0.6744 | 0.42895 | 0.40842 | 0.21689 | [11 empty] | 48 | 24345.7676 | 18653 | 0.76617 | 75 | Fixed | -8.7% | -141.3881 | 2473.4394 | [18 empty] | 1.1538 | 3 | [11 empty] | 13699 | 2085.2123 | 2074.7862 | 2064.4123 | 2054.0902 | 2043.8197 | 2033.6006 | 2023.4326 | 0.95269 |  |  | 0.76617 | -8.7% |  | 0.95269 | -21.6071 | 2043.4286 | -1.098% | -276.4571 | 3759.3429 | -24.4% | 9639.0319 | 4731.4745 | 74860.8686 | 3844 | 17058.2258 | 7432.9031 | 2321.1747 | 1420.2131 | 6363.4808 | 19536.0522 | 8406.2702 | 192.0204 | [11 empty] | 7.331% | 2.7% | 36.83% | 6.687% | 40.38%
49 | 57397 | Dow Jones | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 12 | NJ | 40.3698 | -74.587 | 4.1 | 3.6 | 1515.7875 | Newark | 12.7 | 35.4153 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 4971.783 | 4601 | 5136 | 5016 | 4816 | 4961 | 5147 | 4567 | 4007 | 4818 | 4692 | 4653 | 3409 | 4168 | 0 | [9 empty] | 14 |  | 49 | 0.92542 | 1.0382 | 1.0191 | 0.98334 | 1.018 | 1.0615 | 0.94663 | 0.83473 | 1.0087 | 0.98727 | 0.98399 | 0.72454 | 0.8903 | 0 | [9 empty] | 49 | 67387.428 | 59991 | 0.89024 | 43 | Fixed | -4.461% | -195.5099 | 5751.3956 | [18 empty] | 1.1389 | 1 | [11 empty] | 34244 | 4971.783 | 4946.9241 | 4922.1895 | 4897.5785 | 4873.0906 | 4848.7252 | 4824.4815 | 0.99881 |  |  | 0.89024 | -4.461% |  | 0.99881 | -4.8214 | 4911.2857 | -0.09851% | -421.7857 | 8218 | -11.13% | 93308.4298 | 54923.2704 | 14203.5319 | 5776 | 5449.6033 | 70035.8418 | 96432.4298 | 700090.7959 | 156872.5765 | 478666.3061 | 1154857.2704 | 63720.1837 | 2054103.1888 | 5349969 | [9 empty] | 20.02% | 2.8% | 13.99% | 4.506% | 62.14%
50 | 57589 | Long Island Solar Farm LLC | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Fixed | 28 | NY | 40.8611 | -72.8478 | 37.7 | 31.5 | 1607.1 | Bridgeport | 10.9 | 34.294 | C | 1397 | 663 | 0.489 | 0.47459 | 0% | 1 | 48470.136 | 52713 | 51817 | 50822 | 52287 | 53709 | 47311 | 48760 | 50626 | 48493 | 50059 | 50203 | 45636 | 47878 | 42764 | [9 empty] | 14 |  | 50 | 1.0875 | 1.0744 | 1.0591 | 1.0951 | 1.1305 | 1.0009 | 1.0367 | 1.0818 | 1.0414 | 1.0804 | 1.089 | 0.9949 | 1.049 | 0.94168 | [9 empty] | 50 | 656963.0657 | 693078 | 1.055 | 1 | Fixed | -1.09% | -542.3429 | 53573.1429 | [18 empty] | 1.1968 | 1 | [11 empty] | 357419 | 48470.136 | 48227.7853 | 47986.6464 | 47746.7132 | 47507.9796 | 47270.4397 | 47034.0875 | 1.0693 |  |  | 1.055 | -1.09% |  | 1.0693 | -642.2857 | 53629 | -1.25% | -763.5595 | 56069.75 | -1.589% | 74919.5102 | 278180.898 | 774651.449 | 1505879.5918 | 10833502.0408 | 6072704.0816 | 139129 | 441860.9083 | 496622.2245 | 2640122.0478 | 6413073.8781 | 1615531.787 | 3008572.8458 | 6843020.0069 | [9 empty] | 3.463% | 2% | 57.76% | 3.284% | 60.91%
51 | 57377 | Greater Sandhill | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Tracker | 20 | CO | 37.685 | -105.891 | 20 | 19 | 3068.1 | Alamosa | 5.1 | 39.354 | C | 1926 | 518 | 0.644 | 0.26895 | 5.134% | 0.51565 | 46635.12 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 48862; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 49131; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 47689; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 46378; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 45653; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 47303; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 47210; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 47439; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 46834; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 47760; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 46033; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 43112; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 43350; Median age 14: 13 |  | 51 | 1.0478 | 1.0588 | 1.0329 | 1.0096 | 0.99877 | 1.0401 | 1.0432 | 1.0536 | 1.0454 | 1.0714 | 1.0378 | 0.97686 | 0.98719 | [10 empty] | 51 | 588398.1736 | 606754 | 1.0312 | 3 | Tracker | -0.7406% | -346.9615 | 49102.1154 | [18 empty] | 1.0526 | 1 | [11 empty] | 332226 | 46635.12 | 46401.9444 | 46169.9347 | 45939.085 | 45709.3896 | 45480.8426 | 45253.4384 | 1.0331 |  |  | 1.0312 | -0.7406% |  | 1.0331 | -380.2857 | 48982 | -0.7981% | -751.25 | 53475.0714 | -1.634% | 67748.6531 | 827320.1837 | 23147.449 | 1172579.5918 | 2037960.1837 | 363264.5102 | 792100 | 679.7194 | 14442.889 | 3230749.4694 | 675155.6747 | 1817296.5765 | 128752.8176 | [10 empty] | 1.984% | 3.1% | 156.2% | 1.831% | 169.3%
52 | 57390 | Haleon York RDC Solar Facility | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 5 | PA | 40.0439 | -76.7355 | 3 | 2.6 | 1468.305 | Harrisburg | 11.6 | 33.9623 | C | 1453 | 681 | 0.503 | 0.46869 | 0% | 1 | 3523.932 | 2990 | 3636 | 3544 | 3029 | 3333 | 3307 | 2895 | 2689 | 1862 | 2483 | 2273 | 1120 | 1643 | 798 | [9 empty] | 14 |  | 52 | 0.84848 | 1.037 | 1.0158 | 0.87257 | 0.96497 | 0.96226 | 0.84661 | 0.79032 | 0.55001 | 0.73713 | 0.67817 | 0.33584 | 0.49515 | 0.2417 | [9 empty] | 52 | 47763.2902 | 35602 | 0.74538 | 79 | Fixed | -7.192% | -189.7099 | 3965.8242 | [18 empty] | 1.1538 | 1 | [11 empty] | 22734 | 3523.932 | 3506.3123 | 3488.7808 | 3471.3369 | 3453.9802 | 3436.7103 | 3419.5267 | 0.93553 |  |  | 0.74538 | -7.192% |  | 0.93553 | -41.2143 | 3412.5714 | -1.261% | -266.0119 | 4763.5 | -13.5% | 145433.2704 | 93548.5918 | 65061.4337 | 47835.9388 | 16002.25 | 20082.9388 | 52473.7194 | 2872.4495 | 257447.5115 | 144110.6213 | 189774.3267 | 203723.2704 | 114010.7382 | 58241.7778 | [9 empty] | 12.48% | 2.9% | 23.23% | 7.724% | 37.55%
53 | 57269 | Haverhill | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 20 | MA | 42.8 | -71.1 | 1 | 1 | 1643.625 | Boston | 10.7 | 34.3655 | C | 1432 | 652 | 0.509 | 0.45531 | 0% | 1 | 1314.9 | 989 | 1258 | 1229 | 1121 | 1204 | 1260 | 1098 | 1161 | 897 | 1208 | 1185 | 1048 | 1003 | 1162 | [9 empty] | 14 |  | 53 | 0.75215 | 0.96153 | 0.94409 | 0.86545 | 0.9342 | 0.98257 | 0.86054 | 0.91449 | 0.71009 | 0.9611 | 0.94753 | 0.8422 | 0.81009 | 0.94322 | [9 empty] | 53 | 17822.1232 | 15823 | 0.88783 | 45 | Fixed | -0.532% | -6.0286 | 1175.4286 | [18 empty] | 1 | 1 | [11 empty] | 8159 | 1314.9 | 1308.3255 | 1301.7839 | 1295.275 | 1288.7986 | 1282.3546 | 1275.9428 | 0.89982 |  |  | 0.88783 | -0.532% |  | 0.89982 | 10.9286 | 1121.8571 | 0.942% | 1.0476 | 1084.25 | 0.09565% | 20674.3316 | 13061.2245 | 5528.9847 | 1986.6122 | 756.25 | 5266.6122 | 10071.5561 | 4674.3267 | 38682.4605 | 12830.9559 | 7961.3131 | 2383.5319 | 9000.1362 | 3979.5069 | [9 empty] | 8.748% | 2.5% | 28.58% | 7.765% | 32.19%
54 | 57202 | Jacksonville | 2011 | 2010 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 20 | FL | 30.321 | -81.956 | 15 | 12.6 | 1789.725 | Jacksonville | 20 | 44.7515 | M | 1682 | 735.6 | 0.524 | 0.43734 | 0% | 1 | 21476.7 | 23125 | 21016 | 21397 | 21048 | 20005 | 20587 | 20335 | 17670 | 18314 | 16287 | 16125 | 18361 | 15124 | 11799 | [9 empty] | 14 |  | 54 | 1.0767 | 0.98347 | 1.0063 | 0.99489 | 0.95034 | 0.9829 | 0.97575 | 0.85213 | 0.88763 | 0.79335 | 0.78941 | 0.90339 | 0.74786 | 0.58638 | [9 empty] | 54 | 291094.6789 | 261193 | 0.89728 | 40 | Fixed | -3.494% | -663.5363 | 23633.1648 | [18 empty] | 1.1905 | 1 | [11 empty] | 147513 | 21476.7 | 21369.3165 | 21262.4699 | 21156.1576 | 21050.3768 | 20945.1249 | 20840.3993 | 0.99603 | [6 empty] | -379.2857 | 22590.4286 | -1.784% | -863.131 | 25814.75 | -5.152% | 835134.8776 | 665622.8776 | 3088.1837 | 639.3673 | 474721 | 74139.5102 | 159657.3265 | 1536861.9933 | 71518.0408 | 803605.5274 | 38145.8101 | 8432178.889 | 280849.5261 | 3732302.0069 | [9 empty] | 5.925% | 2.9% | 48.94% | 2.668% | 108.7%
55 | 57525 | Kapaa | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 20 | HI | 22.08 | -159.33 | 1.2 | 1 | 1899.3 | Lihue | 24.2 | 49.766 | M | 1818 | 721.6 | 0.531 | 0.39692 | 0% | 1 | 1823.328 | 1767 | 2070 | 1885 | 1807 | 1857 | 1870 | 1909 | 1614 | 1799 | 1787 | 1735 | 1822 | 1551 | 1497 | [9 empty] | 14 |  | 55 | 0.96911 | 1.141 | 1.0442 | 1.0061 | 1.0391 | 1.0516 | 1.079 | 0.91681 | 1.027 | 1.0253 | 1.0005 | 1.0559 | 0.90338 | 0.87631 | [9 empty] | 55 | 24713.3442 | 24970 | 1.0104 | 7 | Fixed | -1.364% | -24.5011 | 1967.3297 | [18 empty] | 1.2 | 1 | [11 empty] | 13165 | 1823.328 | 1814.2114 | 1805.1403 | 1796.1146 | 1787.134 | 1778.1984 | 1769.3074 | 1.047 | [6 empty] | -0.071429 | 1881 | -0.003798% | -37.881 | 2112 | -2.21% | 12979.7194 | 35775.0204 | 17.7602 | 5433.7959 | 558.9847 | 111.7551 | 812.25 | 38006.4308 | 780.0051 | 2895.4649 | 1575.3339 | 27083.7551 | 4698.7761 | 7168.4444 | [9 empty] | 5.564% | 3.3% | 59.3% | 4.743% | 69.58%
56 | 57412 | Knouse | 2011 | 2010 | Industrial Non-CHP | c-Si | Unknown | Fixed | 32 | PA | 40.026 | -77.234 | 3.2 | 3 | 1643.625 | Harrisburg | 11.6 | 35.2655 | C | 1453 | 681 | 0.503 | 0.46869 | 0% | 1 | 4207.68 | 4237 | 4485 | 4345 | 4234 | 4419 | 4185 | 4020 | 3760 | 4102 | 4123 | 4130 | 4011 | 4205 | 4127 | [9 empty] | 14 |  | 56 | 1.007 | 1.0713 | 1.043 | 1.0215 | 1.0715 | 1.0199 | 0.98457 | 0.92552 | 1.0148 | 1.0251 | 1.032 | 1.0073 | 1.0613 | 1.0469 | [9 empty] | 56 | 57030.7942 | 58383 | 1.0237 | 5 | Fixed | -0.5379% | -22.4901 | 4338.8901 | [18 empty] | 1.0667 | 1 | [11 empty] | 29925 | 4207.68 | 4186.6416 | 4165.7084 | 4144.8799 | 4124.1555 | 4103.5347 | 4083.017 | 1.0313 |  |  | 1.0237 | -0.5379% |  | 1.0313 | -42.0357 | 4443.1429 | -0.9785% | 32.2381 | 3721.25 | 0.7941% | 26931.1543 | 15858.0051 | 782.0013 | 1681 | 34609.287 | 35.148 | 16613.3686 | 48028.8097 | 8209.6543 | 6299.4457 | 2930.16 | 9429.7972 | 4180.2382 | 2077.8403 | [9 empty] | 2.701% | 3.4% | 125.9% | 2.747% | 123.8%
57 | 57381 | Linden | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 20 | NJ | 40.62 | -74.2144 | 3.2 | 2.7 | 1607.1 | Newark | 12.7 | 36.094 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 4114.176 | 3854 | 3894 | 2751 | 3800 | 3900 | 4158 | 3851 | 3873 | 3797 | 4033 | 2872 | 3723 | 3773 | 4118 | [9 empty] | 14 |  | 57 | 0.93676 | 0.95124 | 0.6754 | 0.93763 | 0.96714 | 1.0363 | 0.96461 | 0.975 | 0.96067 | 1.0255 | 0.73396 | 0.95622 | 0.97393 | 1.0683 | [9 empty] | 57 | 55763.4432 | 52397 | 0.93963 | 27 | Fixed | 0.2326% | 8.6967 | 3677.4176 | [18 empty] | 1.1852 | 1 | [11 empty] | 26208 | 4114.176 | 4093.6051 | 4073.1371 | 4052.7714 | 4032.5076 | 4012.345 | 3992.2833 | 0.92377 |  |  | 0.93963 | 0.2326% |  | 0.92377 | 59.5714 | 3505.7143 | 1.604% | -0.16667 | 3756.75 | -0.004439% | 83355.9388 | 72437.8776 | 871288.898 | 3136 | 9298.4694 | 86940.7347 | 5142.9388 | 13825.8403 | 1743.0625 | 77237.6736 | 779541.8403 | 1008.0625 | 339.1736 | 132192.8403 | [9 empty] | 10.44% | 3.1% | 29.69% | 10.74% | 28.87%
58 | 57314 | LA Harbor College | 2012 | 2010 | Commercial Non-CHP | c-Si | MMA | Fixed | 2 | CA | 33.783 | -118.285 | 2.5 | 2.2 | 1862.775 | Long Beach | 17.9 | 43.1945 | M | 1818 | 665 | 0.585 | 0.36579 | 0% | 1 | 3725.55 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3363; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3305; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3096; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3168; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2555; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2747; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 2794; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 0; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 2709; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 3204; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 3104; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 2259; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 2500; Median age 14: 13 |  | 58 | 0.90269 | 0.89158 | 0.83939 | 0.86323 | 0.69969 | 0.75605 | 0.77285 | 0 | 0.75689 | 0.89969 | 0.87599 | 0.64073 | 0.71264 | [10 empty] | 58 | 47005.4932 | 34804 | 0.74042 | 80 | Fixed | -2.574% | -69.8187 | 3165.9615 | [18 empty] | 1.1364 | 2 | [11 empty] | 21028 | 3725.55 | 3706.9223 | 3688.3876 | 3669.9457 | 3651.596 | 3633.338 | 3615.1713 | 0.8185 | [6 empty] | -120.1429 | 3484.5714 | -3.921% | 143.9643 | 927.5 | 6.082% | 2.0408 | 3686.2245 | 792.0204 | 26896 | 108147.0204 | 279.3673 | 22628.7551 | 4323132.0459 | 236022.4605 | 700329.8776 | 351521.9401 | 156872.5765 | 89422.3584 | [10 empty] | 25.42% | 2.4% | 9.442% | 5.071% | 47.33%
59 | 57313 | Metro Support Services | 2011 | 2011 | Commercial Non-CHP | c-Si | Unknown | Fixed | 5 | CA | 34.058 | -118.23 | 1.2 | 1.1 | 1844.5125 | Los Angeles | 17.2 | 42.3588 | M | 1818 | 676 | 0.586 | 0.37184 | 0% | 1 | 1770.732 | 1471 | 1330 | 1325 | 1667 | 1638 | 1576 | 1469 | 1489 | 1089 | 1125 | 1 | 1173 | 479 | 101 | [9 empty] | 14 |  | 59 | 0.83073 | 0.75488 | 0.75582 | 0.95568 | 0.94378 | 0.91262 | 0.85493 | 0.87092 | 0.64016 | 0.66465 | 0.00059377 | 0.69999 | 0.28728 | 0.060879 | [9 empty] | 59 | 24000.4592 | 15933 | 0.66386 | 89 | Fixed | -8.188% | -97.1582 | 1866.7582 | [18 empty] | 1.0909 | 0 | [11 empty] | 10476 | 1770.732 | 1761.8783 | 1753.0689 | 1744.3036 | 1735.5821 | 1726.9042 | 1718.2697 | 0.85793 | [6 empty] | 28.5357 | 1382.4286 | 1.925% | -184.5 | 2803 | -21.31% | 3604.287 | 11990.25 | 20459.2156 | 29045.898 | 12744.7972 | 499.8418 | 12809.389 | 26244 | 2862.25 | 27889 | 596756.25 | 341056 | 5550.25 | 14161 | [9 empty] | 24.69% | 2.3% | 9.314% | 7.625% | 30.16%
60 | 57270 | NEDC Solar Site | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 2.4 | MA | 42.105 | -71.703 | 1 | 1 | 1458.6624 | Worcester | 8.2 | 30.4906 | C | 1416.5 | 693 | 0.503 | 0.48923 | 0% | 1 | 1166.9299 | 1008 | 1054 | 990 | 1037 | 1031 | 1103 | 983 | 994 | 1023 | 1094 | 999 | 1105 | 878 | 979 | [9 empty] | 14 |  | 60 | 0.86381 | 0.90776 | 0.85693 | 0.90212 | 0.90141 | 0.9692 | 0.8681 | 0.88223 | 0.91253 | 0.98076 | 0.9001 | 1.0006 | 0.79905 | 0.89544 | [9 empty] | 60 | 15816.5403 | 14278 | 0.90273 | 39 | Fixed | -0.3137% | -3.2044 | 1043.8901 | [18 empty] | 1 | 1 | [11 empty] | 7206 | 1166.9299 | 1161.0953 | 1155.2898 | 1149.5133 | 1143.7658 | 1138.0469 | 1132.3567 | 0.89549 |  |  | 0.90273 | -0.3137% |  | 0.89549 | 2.2857 | 1020.2857 | 0.2223% | -5.4405 | 1064 | -0.5403% | 212.3265 | 849.3061 | 1379.5918 | 57.3265 | 0.5102 | 4761 | 2839.3673 | 700.9887 | 63.4298 | 7124.1638 | 26.5716 | 11296.6531 | 13288.0512 | 78.0278 | [9 empty] | 5.414% | 2.8% | 51.72% | 3.69% | 75.88%
61 | 57309 | Pacific Cruise | 2011 | 2011 | Commercial Non-CHP | c-Si | Unknown | Fixed | 5 | CA | 33.747 | -118.277 | 1.079 | 1 | 1862.775 | Long Beach | 17.9 | 43.1945 | M | 1818 | 665 | 0.585 | 0.36579 | 0% | 1 | 1607.9474 | 1621 | 1387 | 1605 | 1589 | 0 | 0 | 306 | 26 | 0 | 408 | 547 | 0 | 0 | 0 | [9 empty] | 14 |  | 61 | 1.0081 | 0.86693 | 1.0082 | 1.0032 | 0 | 0 | 0.19612 | 0.016747 | 0 | 0.26545 | 0.35767 | 0 | 0 | 0 | [9 empty] | 61 | 21794.0804 | 7489 | 0.34363 | 100 | Fixed | -20.74% | -123.756 | 1463.0989 | [18 empty] | 1.079 | 0 | [11 empty] | 6508 | 1607.9474 | 1599.9076 | 1591.9081 | 1583.9486 | 1607.9474 | 1607.9474 | 1560.3079 | 0.58316 | [6 empty] | -297.2857 | 2118.8571 | -27.57% | -25.3929 | 427.5 | -15.78% | 40228.898 | 18847.3673 | 142884 | 434657.6531 | 399965.898 | 112320.7347 | 71900.5918 | 39345.5561 | 39586.787 | 54956.7551 | 159058.5319 | 15076.3316 | 9485.3686 | 5184 | [9 empty] | 62.07% | 2.4% | 3.866% | 44.92% | 5.343%
62 | 57367 | Pocono | 2011 | 2010 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 25 | PA | 41.061 | -75.515 | 3 | 2.7 | 1534.05 | Wilkes-Barre | 9.5 | 32.351 | C | 1368 | 707 | 0.48 | 0.51681 | 0% | 1 | 3681.72 | 3831 | 4103 | 3952 | 3918 | 3352 | 3900 | 3142 | 2610 | 3720 | 3743 | 3271 | 3121 | 3087 | 3061 | [9 empty] | 14 |  | 62 | 1.0405 | 1.12 | 1.0842 | 1.0803 | 0.92888 | 1.0862 | 0.87946 | 0.73422 | 1.0517 | 1.0636 | 0.93411 | 0.89575 | 0.89045 | 0.88739 | [9 empty] | 62 | 49901.9449 | 48811 | 0.97814 | 14 | Fixed | -2.016% | -71.0132 | 4019.0989 | [18 empty] | 1.1111 | 1 | [11 empty] | 26198 | 3681.72 | 3663.3114 | 3644.9948 | 3626.7699 | 3608.636 | 3590.5928 | 3572.6399 | 1.0319 |  |  | 0.97814 | -2.016% |  | 1.0319 | -109.75 | 4181.5714 | -2.89% | -5.369 | 3275.75 | -0.1668% | 57994.9605 | 19860.8622 | 9935.8176 | 30775.1837 | 78860.6747 | 142075.148 | 73615.3176 | 387876.8743 | 242626.6122 | 271378.9797 | 2949.5244 | 8157.9605 | 14149.6689 | 19483.5069 | [9 empty] | 8.939% | 2.6% | 29.09% | 6.491% | 40.05%
63 | 57507 | RV CSU Power II | 2011 | 2010 | Commercial Non-CHP | c-Si | MMA | Fixed | 25 | CO | 40.593 | -105.147 | 3.3 | 3 | 1972.35 | Boulder | 10.2 | 36.309 | C | 1689 | 562 | 0.583 | 0.33274 | 0% | 1 | 5207.004 | 4900 | 5083 | 4576 | 3627 | 4411 | 5093 | 4734 | 4419 | 4579 | 3930 | 3832 | 3095 | 2737 | 2746 | [9 empty] | 14 |  | 63 | 0.94104 | 0.98109 | 0.88767 | 0.70712 | 0.86428 | 1.0029 | 0.93692 | 0.87897 | 0.91537 | 0.78958 | 0.77376 | 0.62809 | 0.55823 | 0.56288 | [9 empty] | 63 | 70575.6079 | 57762 | 0.81844 | 62 | Fixed | -3.659% | -153.767 | 5279.1099 | [18 empty] | 1.1 | 1 | [11 empty] | 32424 | 5207.004 | 5180.969 | 5155.0641 | 5129.2888 | 5103.6424 | 5078.1242 | 5052.7335 | 0.903 |  |  | 0.81844 | -3.659% |  | 0.903 | -22.9643 | 4723.8571 | -0.4945% | -319.9524 | 7118.5 | -8.512% | 39643.6543 | 164082.8622 | 6235.3584 | 1010025 | 39218.1441 | 256976.5765 | 29204.3686 | 19566.6808 | 115648.5765 | 121.5244 | 54277.9053 | 33882.2908 | 49336.8713 | 11413.3611 | [9 empty] | 8.762% | 4% | 45.65% | 10.14% | 39.43%
64 | 57579 | Robert O Schulz | 2009 | 2009 | Electric Utility | c-Si | Conergy | Tracker | 0 | CA | 37.858 | -120.8917 | 1.5936 | 1.75 | 2483.7 | Sacramento | 16 | 45.91 | M | 1793 | 572 | 0.608 | 0.31902 | 0% | 1 | 3008.0985 | 2930 | 2920 | 2912 | 3043 | 3067 | 2828 | 2942 | 2732 | 2867 | 2761 | 2710 | 1567 | 2162 | 2132 | 1703 | 2121 | [7 empty] | 16 |  | 64 | 0.97404 | 0.97559 | 0.97781 | 1.0269 | 1.0402 | 0.96399 | 1.0079 | 0.94065 | 0.99209 | 0.96021 | 0.94721 | 0.55046 | 0.76328 | 0.75648 | 0.60729 | 0.76016 | [7 empty] | 64 | 46366.1538 | 41397 | 0.89283 | 42 | Tracker | -3.131% | -82.2985 | 3286.85 | [18 empty] | 0.91063 | 0 | [11 empty] | 20642 | 3008.0985 | 2993.058 | 2978.0927 | 2963.2022 | 2948.3862 | 2933.6443 | 2918.9761 | 0.99511 | [6 empty] | 0.25 | 2947.8571 | 0.008478% | -128.5273 | 3847.7636 | -5.424% | 327.8686 | 804.1276 | 1340.0829 | 8862.8776 | 13898.7258 | 14727.5561 | 57.8686 | 7664.2066 | 30969.6003 | 39405.8592 | 76196.074 | 545288.2631 | 222.281 | 6992.0003 | 47025.8939 | 108684.1071 | [7 empty] | 9.179% | 3.3% | 35.95% | 2.564% | 128.7%
65 | 57524 | Roger Rd. WWTP SunE | 2011 | 2010 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | AZ | 32.2894 | -111.0331 | 1.1 | 1.1 | 2958.525 | Tucson | 20.2 | 53.6395 | H | 2114 | 513 | 0.669 | 0.24267 | 1.577% | 0.81593 | 2473.3269 | 2320 | 2172 | 2153 | 2144 | 1858 | 1810 | 1817 | 1422 | 1025 | 696 | 1203 | 1180 | 1132 | 996 | [9 empty] | 14 |  | 65 | 0.93801 | 0.88258 | 0.87926 | 0.87998 | 0.76643 | 0.75038 | 0.75707 | 0.59547 | 0.43138 | 0.29439 | 0.51139 | 0.50413 | 0.48606 | 0.42981 | [9 empty] | 65 | 33523.4137 | 21928 | 0.65411 | 90 | Tracker | -7.112% | -115.5077 | 2432.5934 | [18 empty] | 1 | 1 | [11 empty] | 14274 | 2473.3269 | 2460.9603 | 2448.6555 | 2436.4122 | 2424.2301 | 2412.109 | 2400.0484 | 0.8369 | 0.65411 | -7.112% |  |  | 0.8369 |  | -90.2857 | 2400.2857 | -4.332% | -74.1071 | 1962 | -6.26% | 100 | 2276.6531 | 555.6122 | 10995.0204 | 8255.0204 | 2359.1837 | 2373.0816 | 2793.8776 | 72919.287 | 275550.0051 | 3156.0319 | 11510.2245 | 17793.6543 | 5112.25 | [9 empty] | 11% | 3% | 27.27% | 3.041% | 98.66%
66 | 57200 | Shelby | 2011 | 2010 | IPP Non-CHP | Si_IBT | Duke | Tracker | 0 | NC | 35.2536 | -81.5956 | 1.035 | 0.94 | 2118.45 | Charlotte | 15.6 | 42.795 | M | 1635 | 689 | 0.534 | 0.42141 | 1.225% | 0.85388 | 1666.3728 | 1823 | 1752 | 1725 | 1777 | 1622 | 1599 | 1725 | 1691 | 1332 | 1488 | 1535 | 1178 | 1111 | 1349 | [9 empty] | 14 |  | 66 | 1.094 | 1.0567 | 1.0456 | 1.0825 | 0.99308 | 0.98392 | 1.0668 | 1.051 | 0.83205 | 0.93416 | 0.96851 | 0.747 | 0.70805 | 0.86405 | [9 empty] | 66 | 22585.9767 | 21707 | 0.96108 | 21 | Tracker | -2.979% | -46.8901 | 1902.1758 | [18 empty] | 1.1011 | 1 | [11 empty] | 12023 | 1666.3728 | 1658.0409 | 1649.7507 | 1641.5019 | 1633.2944 | 1625.128 | 1617.0023 | 1.0463 | [6 empty] | -25.1071 | 1818 | -1.451% | -70.7976 | 2169.5 | -4.964% | 906.4401 | 249.1888 | 312.5319 | 3531.7551 | 4965.2156 | 4672.699 | 6847.5625 | 7723.0618 | 40128.6747 | 700.9887 | 20814.9321 | 20143.7194 | 19080.16 | 29127.1111 | [9 empty] | 6.878% | 3.3% | 47.98% | 3.226% | 102.3%
67 | 57341 | Silver Lake | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 20 | NJ | 40.4948 | -74.3995 | 2 | 1.7 | 1607.1 | Newark | 12.7 | 36.094 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 2571.36 | 2385 | 2623 | 2596 | 2390 | 2434 | 2502 | 2460 | 2330 | 2343 | 2531 | 1914 | 2665 | 2567 | 2531 | [9 empty] | 14 |  | 67 | 0.92752 | 1.0252 | 1.0198 | 0.94355 | 0.96575 | 0.99772 | 0.9859 | 0.93849 | 0.94847 | 1.0297 | 0.78262 | 1.0952 | 1.0602 | 1.0506 | [9 empty] | 67 | 34852.152 | 34271 | 0.98333 | 13 | Fixed | -0.1392% | -3.4088 | 2473.4945 | [18 empty] | 1.1765 | 1 | [11 empty] | 17390 | 2571.36 | 2558.5032 | 2545.7107 | 2532.9821 | 2520.3172 | 2507.7156 | 2495.1771 | 0.98073 |  |  | 0.98333 | -0.1392% |  | 0.98073 | -6.3929 | 2509.8571 | -0.257% | 24.1786 | 2163.75 | 1% | 14033.787 | 15858.0051 | 11092.6033 | 8889.7959 | 1926.5829 | 930.25 | 26.0829 | 738.6747 | 1471.2704 | 15741.287 | 265961.2245 | 44566.2258 | 7908.2908 | 826.5625 | [9 empty] | 6.818% | 3.1% | 45.47% | 3.495% | 88.71%
68 | 56930 | Space Coast | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 20 | FL | 28.486 | -80.681 | 11.5 | 10 | 1899.3 | Daytona Beach | 21.3 | 46.866 | M | 1771 | 769 | 0.546 | 0.43422 | 0.1706% | 0.97823 | 17473.56 | 18842 | 18508 | 18169 | 17551 | 17682 | 18300 | 15557 | 17546 | 16554 | 14798 | 16431 | 14878 | 12814 | 8582 | [9 empty] | 14 |  | 68 | 1.0783 | 1.0645 | 1.0503 | 1.0197 | 1.0324 | 1.0739 | 0.9175 | 1.04 | 0.98614 | 0.88596 | 0.98867 | 0.89972 | 0.7788 | 0.52421 | [9 empty] | 68 | 236836.2149 | 226212 | 0.95514 | 24 | Fixed | -3.359% | -551.9604 | 20297.7033 | [18 empty] | 1.15 | 1 | [11 empty] | 124609 | 17473.56 | 17386.1922 | 17299.2612 | 17212.7649 | 17126.7011 | 17041.0676 | 16955.8623 | 1.0341 | [6 empty] | -384.2143 | 19338.1429 | -2.135% | -903.3333 | 24130 | -6.168% | 12528.0051 | 3808.6531 | 272.25 | 62642.9388 | 70187.148 | 1605651.0204 | 1191684.1276 | 413020.4444 | 306916 | 89201.7778 | 5007152.1111 | 2521744 | 182613.7778 | 8417735.1111 | [9 empty] | 7.376% | 3.2% | 43.38% | 3.645% | 87.8%
69 | 57559 | Sunset Reservoir | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 5 | CA | 37.7509 | -122.482 | 5 | 4.5 | 1771.4625 | San Francisco | 13.9 | 38.5157 | C | 1738 | 576 | 0.583 | 0.33142 | 0% | 1 | 7085.85 | 6751 | 6828 | 2582 | 6640 | 6759 | 6879 | 6545 | 6905 | 6572 | 6531 | 6375 | 6246 | 6028 | 6488 | [9 empty] | 14 |  | 69 | 0.95274 | 0.96845 | 0.36806 | 0.95128 | 0.97319 | 0.99545 | 0.95187 | 1.0093 | 0.96543 | 0.96423 | 0.94593 | 0.93144 | 0.90345 | 0.97728 | [9 empty] | 69 | 96041.4417 | 88129 | 0.91761 | 33 | Fixed | 0.6024% | 37.8044 | 6011.3956 | [18 empty] | 1.1111 | 1 | [11 empty] | 42984 | 7085.85 | 7050.4208 | 7015.1686 | 6980.0928 | 6945.1923 | 6910.4664 | 6875.914 | 0.87968 |  |  | 0.91761 | 0.6024% |  | 0.87968 | 130.75 | 5617.5714 | 2.152% | -70.4524 | 7201 | -1.09% | 1005364.3176 | 900465.4337 | 11749959.7462 | 249428.898 | 237830.389 | 227460.8622 | 148.3176 | 71619.9546 | 25.7194 | 1191.8934 | 2603.4291 | 12005.898 | 66110.2046 | 74711.1111 | [9 empty] | 16.22% | 2.3% | 14.18% | 23.33% | 9.857%
70 | 57402 | Taylorsville | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | NC | 35.909 | -81.152 | 1.2 | 1 | 2118.45 | Charlotte | 15.6 | 42.795 | M | 1635 | 689 | 0.534 | 0.42141 | 3.308% | 0.65265 | 1932.0264 | 1853 | 1772 | 1722 | 1668 | 1688 | 1852 | 1639 | 1598 | 1645 | 1492 | 1538 | 1451 | 1332 | 1013 | [9 empty] | 14 |  | 70 | 0.9591 | 0.92178 | 0.90027 | 0.87642 | 0.89139 | 0.98291 | 0.87423 | 0.85665 | 0.88627 | 0.80788 | 0.83697 | 0.7936 | 0.73217 | 0.55962 | [9 empty] | 70 | 26186.6397 | 22263 | 0.85017 | 55 | Tracker | -2.827% | -45.6066 | 1932.2637 | [18 empty] | 1.2 | 1 | [11 empty] | 12194 | 1932.0264 | 1922.3663 | 1912.7544 | 1903.1907 | 1893.6747 | 1884.2063 | 1874.7853 | 0.91526 | [6 empty] | -18.4286 | 1815.7143 | -1.052% | -74.381 | 2244.5 | -5.082% | 3104.0816 | 47.0204 | 1476.7551 | 5476 | 1265.3265 | 21567.0204 | 2276.6531 | 2647.3475 | 4890.0051 | 75.5244 | 12474.7625 | 9815.148 | 2965.0618 | 36163.3611 | [9 empty] | 5.426% | 3.3% | 60.81% | 4.071% | 81.05%
71 | 57352 | Trenton | 2012 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 20 | NJ | 40.2314 | -74.7539 | 1.3 | 1 | 1643.625 | Philadelphia | 12.4 | 36.0655 | C | 1455 | 671.5 | 0.501 | 0.46151 | 0.595% | 0.92612 | 1709.37 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1617; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1583; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1515; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1599; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1649; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1543; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1470; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 1582; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 1598; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 1179; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 1588; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 1591; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 1575; Median age 14: 13 |  | 71 | 0.94596 | 0.93073 | 0.89522 | 0.94961 | 0.98422 | 0.92558 | 0.88622 | 0.95854 | 0.9731 | 0.72156 | 0.97675 | 0.98351 | 0.97852 | [10 empty] | 71 | 21567.2263 | 20089 | 0.93146 | 29 | Fixed | -0.441% | -6.8297 | 1593.1154 | [18 empty] | 1.3 | 2 | [11 empty] | 10976 | 1709.37 | 1700.8232 | 1692.319 | 1683.8574 | 1675.4382 | 1667.061 | 1658.7257 | 0.93115 |  |  | 0.93146 | -0.441% |  | 0.93115 | -13.8214 | 1623.2857 | -0.8776% | 11.5357 | 1396.5 | 0.763% | 56.787 | 159.8418 | 4465.1033 | 961 | 8991.1033 | 6.9847 | 3196.287 | 8688.9031 | 9541.1033 | 110793.8776 | 4174.0829 | 3144.0051 | 814.287 | [10 empty] | 7.066% | 3.3% | 46.7% | 3.219% | 102.5%
72 | 57392 | UASTP I | 2012 | 2010 | Electric Utility | c-Si | Unknown | Tracker | 0 | AZ | 32.099 | -110.811 | 1.6 | 1.2 | 2958.525 | Tucson | 20.2 | 53.6395 | H | 2114 | 513 | 0.669 | 0.24267 | 11.38% | 0.2304 | 3597.5664 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3038; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3091; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2781; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2550; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1402; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2818; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 2997; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 2203; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 2584; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 1539; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 320; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 403; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 1591; Median age 14: 13 |  | 72 | 0.84446 | 0.86351 | 0.78081 | 0.71955 | 0.3976 | 0.80319 | 0.8585 | 0.63423 | 0.74765 | 0.44753 | 0.093521 | 0.11837 | 0.46966 | [10 empty] | 72 | 45390.7162 | 27317 | 0.60182 | 94 | Tracker | -8.332% | -182.6923 | 3380.1538 | [18 empty] | 1.3333 | 2 | [11 empty] | 18677 | 3597.5664 | 3579.5786 | 3561.6807 | 3543.8723 | 3526.1529 | 3508.5221 | 3490.9795 | 0.75285 | 0.60182 | -8.332% |  |  | 0.75285 |  | -73.1429 | 2960.7143 | -2.704% | -360.0714 | 5263.1429 | -21.66% | 22628.7551 | 76491.7551 | 1577.2245 | 13957.7347 | 1423249 | 87700.5918 | 300617.2245 | 32245.898 | 315282.25 | 15234.6122 | 965025.5561 | 290829.0816 | 1017648.6173 | [10 empty] | 28.19% | 3% | 10.64% | 19.66% | 15.26%
73 | 57383 | WEA Texas Bayonne | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 13 | NJ | 40.6772 | -74.0919 | 1.7 | 1.5 | 1515.7875 | Newark | 12.7 | 35.4153 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 2061.471 | 1991 | 2073 | 1772 | 1746 | 2142 | 1464 | 1801 | 1974 | 1147 | 1452 | 2010 | 2169 | 2059 | 2015 | [9 empty] | 14 |  | 73 | 0.96582 | 1.0106 | 0.86824 | 0.8598 | 1.0601 | 0.7282 | 0.90032 | 0.99176 | 0.57916 | 0.73685 | 1.0252 | 1.1118 | 1.0607 | 1.0433 | [9 empty] | 73 | 27941.1287 | 25815 | 0.92391 | 31 | Fixed | 0.1612% | 2.9692 | 1821.6593 | [18 empty] | 1.1333 | 1 | [11 empty] | 12989 | 2061.471 | 2051.1636 | 2040.9078 | 2030.7033 | 2020.5498 | 2010.447 | 2000.3948 | 0.91371 |  |  | 0.92391 | 0.1612% |  | 0.91371 | -50.6429 | 2058.1429 | -2.692% | 66.0357 | 1135 | 3.612% | 272.25 | 13489.1633 | 18013.4745 | 12005.898 | 113617.148 | 84265.7959 | 9478.4133 | 96543.3673 | 339098.2462 | 117894.1276 | 22084.0829 | 58356.7551 | 4294.9298 | 1980.25 | [9 empty] | 13.68% | 2.8% | 20.46% | 10.21% | 27.43%
74 | 57203 | Wyandot | 2011 | 2010 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 25 | OH | 40.8795 | -83.317 | 12 | 10 | 1534.05 | Mansfield | 9.7 | 32.551 | C | 1390 | 716.6 | 0.485 | 0.51554 | 0% | 1 | 14726.88 | 14068 | 15763 | 14203 | 14593 | 14582 | 14398 | 13609 | 13045 | 12511 | 11825 | 13165 | 12700 | 10243 | 11815 | 10477 | [8 empty] | 15 |  | 74 | 0.95526 | 1.0757 | 0.97414 | 1.0059 | 1.0102 | 1.0025 | 0.95231 | 0.91743 | 0.88429 | 0.84001 | 0.93989 | 0.91125 | 0.73865 | 0.85629 | 0.76314 | [8 empty] | 74 | 213336.6209 | 196997 | 0.92341 | 32 | Fixed | -2.33% | -309.6143 | 15610.0476 | [18 empty] | 1.2 | 1 | [11 empty] | 101216 | 14726.88 | 14653.2456 | 14579.9794 | 14507.0795 | 14434.5441 | 14362.3714 | 14290.5595 | 0.99667 |  |  | 0.92341 | -2.33% |  | 0.99667 | -133.1429 | 14992 | -0.9166% | -331.3167 | 15798.9278 | -2.726% | 625455.0204 | 1075961.6531 | 151765.898 | 17841.3265 | 65389.7959 | 41966.449 | 203401 | 10690.4111 | 93683.606 | 436605.246 | 1021222.5309 | 768904.8941 | 1559529.1912 | 428377.5223 | 124029.1872 | [8 empty] | 5.06% | 3.7% | 73.12% | 3.861% | 95.83%
75 | 57382 | Yardville | 2011 | 2010 | Electric Utility | c-Si | Unknown | Fixed | 15 | NJ | 40.1688 | -74.6567 | 4.3 | 3.6 | 1552.3125 | Philadelphia | 12.4 | 35.3867 | C | 1455 | 671.5 | 0.501 | 0.46151 | 0% | 1 | 5339.955 | 4616 | 5700 | 5467 | 5460 | 5675 | 5769 | 5312 | 5016 | 5121 | 5419 | 3852 | 5820 | 5362 | 5551 | [9 empty] | 14 |  | 75 | 0.86443 | 1.0728 | 1.0341 | 1.038 | 1.0843 | 1.1078 | 1.0251 | 0.97288 | 0.99823 | 1.0616 | 0.75843 | 1.15 | 1.0664 | 1.1095 | [9 empty] | 75 | 72377.6225 | 74140 | 1.0243 | 4 | Fixed | -0.1311% | -6.9495 | 5347.8352 | [18 empty] | 1.1944 | 1 | [11 empty] | 37999 | 5339.955 | 5313.2552 | 5286.6889 | 5260.2555 | 5233.9542 | 5207.7845 | 5181.7455 | 1.0319 |  |  | 1.0243 | -0.1311% |  | 1.0319 | 86.9286 | 5080.7143 | 1.614% | 46.8214 | 4690 | 0.9036% | 304309.8418 | 198406.6122 | 15750.25 | 996.7551 | 25485.8418 | 27793.6531 | 142290.6173 | 2359.1837 | 92.2972 | 68009.1888 | 1830705.6441 | 322786.3061 | 4009.6033 | 42230.25 | [9 empty] | 8.72% | 3.1% | 35.55% | 5.888% | 52.65%
76 | 57422 | Yolo County | 2011 | 2010 | Commercial Non-CHP | Si_IBT | SunPower | Tracker | 0 | CA | 38.6597 | -121.7294 | 1.1 | 1 | 2483.7 | Sacramento | 16 | 45.91 | M | 1793 | 572 | 0.608 | 0.31902 | 1.833% | 0.78939 | 2076.3732 | 2034 | 2041 | 2041 | 2021 | 2037 | 1940 | 1930 | 1869 | 1106 | 1332 | 1298 | 533 | 534 | 0 | [9 empty] | 14 |  | 76 | 0.97959 | 0.9879 | 0.99287 | 0.98808 | 1.0009 | 0.95803 | 0.95789 | 0.93227 | 0.55445 | 0.67111 | 0.65726 | 0.27125 | 0.27312 | 0 | [9 empty] | 76 | 28143.1128 | 20716 | 0.73609 | 82 | Tracker | -9.579% | -148.8791 | 2596.3077 | [18 empty] | 1.1 | 1 | [11 empty] | 14044 | 2076.3732 | 2065.9913 | 2055.6614 | 2045.3831 | 2035.1562 | 2024.9804 | 2014.8555 | 0.98084 | [6 empty] | -18.5 | 2080.2857 | -0.9179% | -261.1667 | 3817.5 | -24.29% | 772.0459 | 5.2245 | 262.9031 | 216.5102 | 2422.0459 | 857.6531 | 432.0459 | 19834.0278 | 130321 | 15918.0278 | 124844.4444 | 22650.25 | 12469.4444 | 25974.6944 | [9 empty] | 10.79% | 3.3% | 30.58% | 1.328% | 248.5%
77 | 57310 | 1420 Coil Av #C | 2011 | 2011 | Commercial Non-CHP | c-Si | Unknown | Fixed | 10 | CA | 33.795 | -118.241 | 1.3 | 1 | 1917.5625 | Long Beach | 17.9 | 43.6017 | M | 1818 | 665 | 0.585 | 0.36579 | 0.9912% | 0.87998 | 1994.265 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1992; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2173; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1528; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2149; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1515; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1592; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1660; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 2139; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 1781; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 1713; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 1509; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 0; Median age 14: 12 |  | 77 | 0.99886 | 1.0951 | 0.77392 | 1.0939 | 0.77506 | 0.81855 | 0.8578 | 1.1109 | 0.9296 | 0.8986 | 0.79556 | 0 | [11 empty] | 77 | 23283.9186 | 19751 | 0.84827 | 56 | Fixed | -5.474% | -92.6329 | 2248.0303 | [18 empty] | 1.3 | 0 | [11 empty] | 12609 | 1994.265 | 1984.2937 | 1974.3722 | 1964.5003 | 1954.6778 | 1944.9045 | 1935.1799 | 0.91687 | [6 empty] | -77.5357 | 2111.4286 | -4.214% | -293.0857 | 4251.3143 | -19.98% | 1755.0115 | 46934.1276 | 123075.6747 | 120905.2245 | 43576.5625 | 2939.1888 | 8339.6033 | 53996.4808 | 28041.8947 | 154089.8947 | 231966.0808 | 539175.5102 | [11 empty] | 20.41% | 2.6% | 12.74% | 12.37% | 21.02%
78 | 57458 | 145 Talmadge | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Fixed | 10 | NJ | 40.536 | -74.3913 | 4.3 | 3.8 | 1515.7875 | Newark | 12.7 | 35.4153 | C | 1412 | 685 | 0.492 | 0.48513 | 0% | 1 | 5214.309 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 5173; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 5036; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 4524; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 4802; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 5051; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 4819; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 4626; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 5010; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 4844; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 4629; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 5254; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 4644; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 4844; Median age 14: 13 |  | 78 | 0.99208 | 0.97066 | 0.87635 | 0.93488 | 0.9883 | 0.94764 | 0.91426 | 0.99513 | 0.96699 | 0.92872 | 1.0594 | 0.94111 | 0.98658 | [10 empty] | 78 | 65789.2569 | 63256 | 0.96149 | 20 | Fixed | -0.1981% | -9.6484 | 4933.3846 | [18 empty] | 1.1316 | 1 | [11 empty] | 34031 | 5214.309 | 5188.2375 | 5162.2963 | 5136.4848 | 5110.8024 | 5085.2484 | 5059.8221 | 0.94643 |  |  | 0.96149 | -0.1981% |  | 0.94643 | -55.2857 | 5082.7143 | -1.131% | 11.8571 | 4717.2857 | 0.2452% | 21191.0408 | 4077.7347 | 154336.7347 | 3548.7551 | 59885.0816 | 4624 | 4860.0816 | 39147.449 | 400 | 42789.8776 | 165068.0816 | 46471.0408 | 752.3265 | [10 empty] | 4.216% | 2.8% | 66.41% | 3.907% | 71.67%
79 | 57652 | Yamhill Solar LLC | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Fixed | 28 | OR | 45.1089 | -123.2786 | 1.2 | 1 | 1534.05 | Salem | 11.2 | 34.051 | C | 1370 | 632 | 0.505 | 0.46131 | 0% | 1 | 1472.688 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1280; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1341; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1209; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1327; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1223; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 914; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1192; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 1206; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 143; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 1006; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 1033; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 955; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 881; Median age 14: 13 |  | 79 | 0.86916 | 0.91516 | 0.82922 | 0.91473 | 0.84727 | 0.63639 | 0.83412 | 0.84815 | 0.10107 | 0.71463 | 0.73749 | 0.68523 | 0.63531 | [10 empty] | 79 | 18580.995 | 13710 | 0.73785 | 81 | Fixed | -4.012% | -43.1813 | 1356.8846 | [18 empty] | 1.2 | 1 | [11 empty] | 8486 | 1472.688 | 1465.3246 | 1457.9979 | 1450.7079 | 1443.4544 | 1436.2371 | 1429.056 | 0.83561 |  |  | 0.73785 | -4.012% |  | 0.83561 | -39.4286 | 1370 | -3.2% | -19.4643 | 1111.2143 | -2.124% | 2557.4694 | 2485.7347 | 1824.5102 | 13159.3673 | 2514.3061 | 48148.898 | 9604 | 62750.25 | 628905.6441 | 7997.4694 | 18466.8686 | 5984.1276 | 520.8176 | [10 empty] | 23.59% | 4.1% | 17.38% | 8.835% | 46.41%
80 | 57554 | AFA Solar Farm | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | CO | 38.9579 | -104.806 | 6 | 5.5 | 2447.175 | Colorado Springs | 9.2 | 38.8385 | C | 1726.5 | 544.7 | 0.587 | 0.31549 | 1.097% | 0.86803 | 11159.118 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 12385; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 11270; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 11294; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 11205; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 11563; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 11203; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 11799; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 11093; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 11147; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 11577; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 11444; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 10963; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 10866; Median age 14: 13 |  | 80 | 1.1099 | 1.015 | 1.0223 | 1.0193 | 1.0572 | 1.0294 | 1.0896 | 1.0296 | 1.0398 | 1.0853 | 1.0782 | 1.0381 | 1.0341 | [10 empty] | 80 | 140795.2772 | 147809 | 1.0498 | 2 | Tracker | -0.4761% | -54.2582 | 11749.7308 | [18 empty] | 1.0909 | 1 | [11 empty] | 80719 | 11159.118 | 11103.3224 | 11047.8058 | 10992.5668 | 10937.6039 | 10882.9159 | 10828.5013 | 1.049 |  |  | 1.0498 | -0.4761% |  | 1.049 | -57.9643 | 11763.1429 | -0.5014% | -98.6429 | 12256.2857 | -0.8753% | 462157.1747 | 142290.6173 | 87172.5625 | 106462.3673 | 8042.2462 | 45095.5561 | 195016.8686 | 139982.8776 | 49062.25 | 94336.7347 | 74412.0459 | 12005.898 | 11648.5765 | [10 empty] | 2.915% | 4.1% | 140.7% | 3.353% | 122.3%
81 | 57697 | Aerojet I | 2011 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | CA | 38.613 | -121.163 | 3.6 | 3 | 2483.7 | Sacramento | 16 | 45.91 | M | 1793 | 572 | 0.608 | 0.31902 | 4.302% | 0.57409 | 6795.4032 | 6514 | 6849 | 7109 | 6380 | 6363 | 5725 | 5120 | 5028 | 5923 | 5725 | 5916 | 5919 | 5891 | 5144 | [9 empty] | 14 |  | 81 | 0.95859 | 1.013 | 1.0567 | 0.9531 | 0.95533 | 0.86386 | 0.77645 | 0.76633 | 0.90728 | 0.88136 | 0.91534 | 0.92041 | 0.92065 | 0.80795 | [9 empty] | 81 | 92104.7327 | 83606 | 0.90773 | 36 | Tracker | -1.642% | -98.8879 | 6713.5165 | [18 empty] | 1.2 | 0 | [11 empty] | 44060 | 6795.4032 | 6761.4262 | 6727.6191 | 6693.981 | 6660.5111 | 6627.2085 | 6594.0725 | 0.94024 | [6 empty] | -256.2857 | 7319.4286 | -3.99% | 55.5 | 5000.5 | 0.994% | 301557.8776 | 1776.0204 | 311842.4694 | 7346.9388 | 105625 | 3216.5102 | 164372.3265 | 173472.25 | 178929 | 28730.25 | 93025 | 63756.25 | 28561 | 401322.25 | [9 empty] | 6.109% | 3.3% | 54.02% | 5.683% | 58.07%
82 | 57698 | Aerojet II | 2011 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | CA | 38.609 | -121.17 | 2.4 | 2.2 | 2483.7 | Sacramento | 16 | 45.91 | M | 1793 | 572 | 0.608 | 0.31902 | 1.609% | 0.81257 | 4530.2688 | 4361 | 4569 | 4743 | 4230 | 3945 | 3861 | 2945 | 3892 | 3994 | 3752 | 4042 | 3826 | 3739 | 3846 | [9 empty] | 14 |  | 82 | 0.96264 | 1.0136 | 1.0575 | 0.94787 | 0.88845 | 0.8739 | 0.66992 | 0.88979 | 0.9177 | 0.86643 | 0.93808 | 0.89242 | 0.87651 | 0.90612 | [9 empty] | 82 | 61403.1551 | 55745 | 0.90785 | 35 | Tracker | -1.371% | -54.9736 | 4394.0879 | [18 empty] | 1.0909 | 0 | [11 empty] | 28654 | 4530.2688 | 4507.6175 | 4485.0794 | 4462.654 | 4440.3407 | 4418.139 | 4396.0483 | 0.91722 | [6 empty] | -230.7857 | 5016.5714 | -5.483% | 63.4286 | 3088.5 | 1.689% | 180442.9031 | 196 | 175381.4745 | 18651.7551 | 6782.699 | 52506.449 | 208001.148 | 87658.2908 | 111985.8418 | 853.4745 | 65426.3316 | 558.9847 | 30300.8622 | 17030.25 | [9 empty] | 6.562% | 3.3% | 50.29% | 7.398% | 44.61%
83 | 57577 | Alamogordo Solar Energy Center | 2012 | 2011 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 25 | NM | 32.866 | -106 | 6.4 | 5 | 2337.6 | El Paso | 17.3 | 46.124 | M | 2113 | 580 | 0.667 | 0.27449 | 2.956% | 0.68295 | 11968.512 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 12062; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 11735; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 11267; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 11046; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 11552; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 11421; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 11097; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 11031; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 11513; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 10916; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 11015; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 11300; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 11160; Median age 14: 13 |  | 83 | 1.0078 | 0.98542 | 0.95087 | 0.93691 | 0.98475 | 0.97847 | 0.95549 | 0.95458 | 1.0013 | 0.95415 | 0.96764 | 0.99766 | 0.99026 | [10 empty] | 83 | 151007.4511 | 147115 | 0.97422 | 16 | Fixed | -0.4579% | -51.9396 | 11680.1154 | [18 empty] | 1.28 | 1 | [11 empty] | 80180 | 11968.512 | 11908.6694 | 11849.1261 | 11789.8805 | 11730.9311 | 11672.2764 | 11613.915 | 0.97149 | [6 empty] | -115.6429 | 11916.8571 | -1.005% | 8.1786 | 11065.6429 | 0.07337% | 68009.1888 | 2443.1837 | 91765.7194 | 166697.2245 | 45521.2704 | 39204 | 107.2704 | 10014.2908 | 139689.0625 | 53559.1837 | 19770.3686 | 18554.3316 | 143.1441 | [10 empty] | 1.984% | 2.3% | 115.9% | 2.123% | 108.4%
84 | 57567 | Albuquerque Solar Energy Center | 2011 | 2011 | IPP Non-CHP | CdSCdTe | First Solar | Fixed | 25 | NM | 35.169 | -106.6 | 2.4 | 2 | 2301.075 | Albuquerque | 13.4 | 41.9525 | M | 2047.5 | 573 | 0.667 | 0.27985 | 0.8376% | 0.89758 | 4418.064 | 3384 | 0 | 3715 | 4458 | 4185 | 4370 | 4310 | 4280 | 4173 | 3793 | 3749 | 4198 | 3984 | 4075 | [9 empty] | 14 |  | 84 | 0.76595 | 0 | 0.84934 | 1.0243 | 0.96643 | 1.0142 | 1.0053 | 1.0033 | 0.98318 | 0.89814 | 0.89218 | 1.0041 | 0.95766 | 0.98445 | [9 empty] | 84 | 59882.3339 | 52674 | 0.87963 | 50 | Fixed | 2.941% | 109.033 | 2944.6813 | [18 empty] | 1.2 | 0 | [11 empty] | 24422 | 4418.064 | 4418.064 | 4373.9938 | 4352.1238 | 4330.3632 | 4308.7114 | 4287.1679 | 0.80102 | [6 empty] | 428.1429 | 1776.2857 | 13.07% | -36.8333 | 4457 | -0.9049% | 1391388.7551 | 6930432.3265 | 428089.7959 | 939237.8776 | 71824 | 617.8776 | 214633.6531 | 13845.4444 | 2256.25 | 87418.7778 | 91708.0278 | 33489 | 34.0278 | 17866.7778 | [9 empty] | 22.71% | 3.6% | 15.85% | 34.22% | 10.52%
85 | 57765 | Arizona Western College PV | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | AZ | 32.688 | -114.496 | 5.6 | 4.7 | 2922 | Phoenix | 22.6 | 55.768 | H | 2117 | 566 | 0.678 | 0.26736 | 7.587% | 0.37581 | 12436.032 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 9615; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 9062; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 8017; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 9960; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 9854; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 9020; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 8942; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 8165; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 7912; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 8475; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 6148; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 5559; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 1531; Median age 14: 13 |  | 85 | 0.77316 | 0.73235 | 0.65115 | 0.81303 | 0.80842 | 0.74372 | 0.74099 | 0.68001 | 0.66225 | 0.71294 | 0.51978 | 0.47235 | 0.13074 | [10 empty] | 85 | 156906.1796 | 102260 | 0.65173 | 91 | Tracker | -5.614% | -454.3352 | 11046.5 | [18 empty] | 1.1915 | 1 | [11 empty] | 64470 | 12436.032 | 12373.8518 | 12311.9826 | 12250.4227 | 12189.1706 | 12128.2247 | 12067.5836 | 0.75177 | 0.65173 | -5.614% |  |  | 0.75177 |  | -9.5 | 9248 | -0.1031% | -1043.1786 | 17107.7857 | -15.63% | 141752.25 | 27889 | 1446006.25 | 562500 | 427062.25 | 29241 | 57360.25 | 356835.5561 | 37180.1033 | 3236401 | 265408.9605 | 939653.2704 | 4062096.287 | [10 empty] | 12% | 3.6% | 29.99% | 6.733% | 53.47%
86 | 57481 | Chittenden County Solar Partners | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 44.436 | VT | 44.436 | -73.145 | 2.2 | 2.2 | 2045.4 | Burlington | 7 | 33.652 | C | 1374 | 676 | 0.503 | 0.49199 | 0.6884% | 0.91503 | 3419.9088 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3388; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3120; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3228; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3393; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3339; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 3003; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 3085; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 3184; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 3122; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 2991; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 3200; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 2817; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 2853; Median age 14: 13 |  | 86 | 0.99067 | 0.91689 | 0.95339 | 1.0072 | 0.99612 | 0.90038 | 0.92961 | 0.96427 | 0.95024 | 0.91494 | 0.9838 | 0.8704 | 0.88595 | [10 empty] | 86 | 43149.1994 | 40723 | 0.94377 | 25 | Tracker | -1.098% | -34.5934 | 3374.6923 | [18 empty] | 1 | 1 | [11 empty] | 22556 | 3419.9088 | 3402.8093 | 3385.7952 | 3368.8662 | 3352.0219 | 3335.2618 | 3318.5855 | 0.95644 |  |  | 0.94377 | -1.098% |  | 0.95644 | -36.8571 | 3369.7143 | -1.137% | -48.2857 | 3518.8571 | -1.59% | 3040.7347 | 30976 | 969.8776 | 29143.3673 | 23584.1837 | 21191.0408 | 713.6531 | 2644.898 | 1422.3673 | 2025 | 45065.2245 | 14988.7551 | 1454.8776 | [10 empty] | 3.727% | 4.1% | 110% | 3.884% | 105.6%
87 | 57561 | Cotton Center Solar Hybrid | 2012 | 2011 | Electric Utility | c-Si | Unknown | Tracker | 0 | AZ | 33.035 | -112.662 | 21 | 17 | 2922 | Phoenix | 22.6 | 55.768 | H | 2117 | 566 | 0.678 | 0.26736 | 8.859% | 0.31893 | 46635.12 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 46172; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 43658; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 43648; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 42798; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 38993; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 32594; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 36792; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 39075; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 39081; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 40865; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 34814; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 41151; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 39439; Median age 14: 13 |  | 87 | 0.99007 | 0.94087 | 0.94538 | 0.93162 | 0.85306 | 0.71665 | 0.81302 | 0.86781 | 0.8723 | 0.91671 | 0.78489 | 0.93242 | 0.89812 | [10 empty] | 87 | 588398.1736 | 519080 | 0.88219 | 48 | Tracker | -1.196% | -480.2802 | 43291.1923 | [18 empty] | 1.2353 | 1 | [11 empty] | 284655 | 46635.12 | 46401.9444 | 46169.9347 | 45939.085 | 45709.3896 | 45480.8426 | 45253.4384 | 0.88515 | 0.88219 | -1.196% |  |  | 0.88515 |  | -1961.5357 | 48511.1429 | -4.71% | 279.5 | 35950.2857 | 0.7214% | 142587.1543 | 865032.8622 | 1043389.287 | 4549689 | 83830.9298 | 17205311.4337 | 4046563.2972 | 789813.0816 | 378488.6173 | 4493188.6531 | 17730716.3316 | 3410353.6531 | 20962.9031 | [10 empty] | 5.14% | 3.6% | 70.04% | 4.913% | 73.28%
88 | 57337 | Dover Sun Park | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | DE | 39.184 | -75.504 | 11.3 | 10 | 1935.825 | Wilmington DE | 12.3 | 38.1375 | C | 1491 | 670 | 0.513 | 0.44936 | 0.7006% | 0.91358 | 16624.8651 | 18535 | 18152 | 17792 | 17439 | 17596 | 16591 | 16164 | 17225 | 15902 | 17122 | 16578 | 16370 | 12632 | 12004 | [9 empty] | 14 |  | 88 | 1.1149 | 1.0973 | 1.081 | 1.0649 | 1.0799 | 1.0233 | 1.002 | 1.0731 | 0.99566 | 1.0774 | 1.0484 | 1.0405 | 0.80693 | 0.77067 | [9 empty] | 88 | 225333.0245 | 230102 | 1.0212 | 6 | Tracker | -2.219% | -368.844 | 19202.1868 | [18 empty] | 1.13 | 1 | [11 empty] | 122269 | 16624.8651 | 16541.7408 | 16459.0321 | 16376.7369 | 16294.8532 | 16213.379 | 16132.3121 | 1.0665 |  |  | 1.0212 | -2.219% |  | 1.0665 | -372.5357 | 18957.1429 | -2.11% | -609.8214 | 21902.75 | -3.934% | 2460.8686 | 3608.5765 | 2259.6441 | 784 | 251538.0727 | 17142.2908 | 34370.5115 | 40329.2462 | 262509.8418 | 1735712.1441 | 1913479.3673 | 3186607.5115 | 1803840.8622 | 1853001.5625 | [9 empty] | 5.419% | 3.7% | 68.27% | 1.209% | 306%
89 | 57498 | Five Points Solar Station | 2012 | 2011 | Electric Utility | c-Si | PG&E | Fixed | 25 | CA | 36.4 | -120.103 | 17.6 | 15 | 2081.925 | Fresno | 17.4 | 44.3235 | M | 1910 | 578 | 0.634 | 0.30262 | 0% | 1 | 29313.504 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 29948; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 28338; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 28299; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 25471; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 29839; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 27708; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 28699; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 26209; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 24140; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 20947; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 17984; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 18872; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 15412; Median age 14: 13 |  | 89 | 1.0216 | 0.97158 | 0.97512 | 0.88208 | 1.0385 | 0.96922 | 1.0089 | 0.92602 | 0.85721 | 0.74756 | 0.64504 | 0.68029 | 0.55836 | [10 empty] | 89 | 369850.2805 | 321866 | 0.87026 | 52 | Fixed | -4.39% | -1111.4011 | 32538.7308 | [18 empty] | 1.1733 | 1 | [11 empty] | 198302 | 29313.504 | 29166.9365 | 29021.1018 | 28875.9963 | 28731.6163 | 28587.9582 | 28445.0184 | 0.981 | [6 empty] | -123.8214 | 28824.1429 | -0.4361% | -2167.5357 | 43427.2143 | -9.965% | 1556701.8176 | 56882.25 | 23617.1033 | 8167347.449 | 2669839.287 | 139288.9031 | 549981.1543 | 14901.4337 | 48667.5115 | 647795.0204 | 2561028.6747 | 2117648.6173 | 26487.5625 | [10 empty] | 4.829% | 3.6% | 74.56% | 4.841% | 74.37%
90 | 57563 | Hyder | 2012 | 2011 | Electric Utility | c-Si | Unknown | Tracker | 0 | AZ | 33.026 | -113.344 | 18.8 | 17 | 2922 | Phoenix | 22.6 | 55.768 | H | 2117 | 566 | 0.678 | 0.26736 | 5.1% | 0.51793 | 41749.536 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 39252; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 41430; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 41990; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 42004; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 40655; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 38483; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 37780; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 37173; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 36347; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 40609; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 40233; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 40223; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 37777; Median age 14: 13 |  | 90 | 0.94018 | 0.99733 | 1.0159 | 1.0213 | 0.9935 | 0.94515 | 0.93255 | 0.92218 | 0.90622 | 1.0176 | 1.0132 | 1.018 | 0.96095 | [10 empty] | 90 | 526756.4601 | 513956 | 0.9757 | 15 | Tracker | -0.4994% | -197.9341 | 40920.6154 | [18 empty] | 1.1059 | 1 | [11 empty] | 281594 | 41749.536 | 41540.7883 | 41333.0844 | 41126.419 | 40920.7869 | 40716.1829 | 40512.602 | 0.9781 | 0.9757 | -0.4994% |  |  | 0.9781 |  | -415.8929 | 41891.2857 | -1.029% | 356.3214 | 35028.5 | 0.9233% | 4943475.7972 | 137270.25 | 1812773.7258 | 3155190.9388 | 710950.1033 | 833438.5765 | 1440085.7156 | 498536.8622 | 3566027.5829 | 4069441.6531 | 1651133.2156 | 843904.699 | 3548244.9605 | [10 empty] | 3.659% | 3.6% | 98.38% | 3.392% | 106.1%
91 | 57982 | Meridian Vineyards | 2011 | 2010 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | CA | 35.67 | -120.57 | 1.3 | 1.1 | 2142.9217 | Santa Maria | 14.1 | 41.4769 | M | 1893.5 | 572 | 0.616 | 0.30209 | 0% | 1 | 2228.6386 | 2042 | 2060 | 1919 | 0 | 1981 | 1837 | 1759 | 1663 | 1340 | 1516 | 1719 | 1507 | 1418 | 1046 | [9 empty] | 14 |  | 91 | 0.91625 | 0.92898 | 0.86974 | 0 | 0.90689 | 0.84519 | 0.81337 | 0.77284 | 0.62586 | 0.71163 | 0.81097 | 0.71453 | 0.67571 | 0.50095 | [9 empty] | 91 | 30206.9146 | 21807 | 0.72192 | 85 | Fixed | -2.177% | -34.2791 | 1814.7363 | [18 empty] | 1.1818 | 1 | [11 empty] | 11598 | 2228.6386 | 2217.4954 | 2206.4079 | 2228.6386 | 2184.399 | 2173.477 | 2162.6097 | 0.75304 | [6 empty] | -44.0357 | 1833 | -2.623% | -65.619 | 2185 | -4.386% | 64027.0727 | 99270.0051 | 47570.7258 | 2745175.5918 | 135555.4605 | 71938.9031 | 54873.0625 | 8.7166 | 64733.898 | 164.0839 | 65438.5125 | 11974.6122 | 7404.1927 | 48546.7778 | [9 empty] | 31.72% | 3% | 9.459% | 40.92% | 7.331%
92 | 57879 | Perdue Salisbury Photovoltaic | 2012 | 2011 | Electric Utility | c-Si | Unknown | Fixed | 30 | MD | 38.3736 | -75.535 | 1.2 | 1 | 1680.15 | Baltimore | 12.8 | 36.737 | C | 1482 | 646 | 0.506 | 0.4359 | 0% | 1 | 1612.944 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1713; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1609; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1606; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1476; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1674; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1647; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 1229; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 1606; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 0; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 0; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 1551; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 1512; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 1446; Median age 14: 13 |  | 92 | 1.062 | 1.0026 | 1.0057 | 0.92896 | 1.0589 | 1.047 | 0.78522 | 1.0313 | 0 | 0 | 1.011 | 0.99056 | 0.95208 | [10 empty] | 92 | 20350.6135 | 17069 | 0.83875 | 59 | Fixed | -4.149% | -55.6264 | 1702.3846 | [18 empty] | 1.2 | 1 | [11 empty] | 10954 | 1612.944 | 1604.8793 | 1596.8549 | 1588.8706 | 1580.9263 | 1573.0216 | 1565.1565 | 0.98484 |  |  | 0.83875 | -4.149% |  | 0.98484 | -46.7143 | 1751.7143 | -2.941% | 71.9286 | 329.8571 | 6.856% | 64 | 2429.0816 | 31.0408 | 7895.5918 | 24291.449 | 30825.3265 | 38304.0816 | 491000.5102 | 954947.7602 | 1100700.7347 | 184838.5765 | 101761 | 32786.8622 | [10 empty] | 36.4% | 3% | 8.241% | 7.783% | 38.54%
93 | 57671 | SMUD at Fleshman | 2012 | 2011 | IPP Non-CHP | CdSCdTe | Other utility | Fixed | 20 | CA | 38.238 | -121.337 | 3.7 | 2.9 | 1968.6975 | Sacramento | 16 | 42.0819 | M | 1793 | 572 | 0.608 | 0.31902 | 0% | 1 | 5827.3446 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 5868; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 6423; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 5847; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 5676; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 5458; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 5290; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 5513; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 5504; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 5500; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 5502; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 5422; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 4091; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 4963; Median age 14: 13 |  | 93 | 1.007 | 1.1078 | 1.0135 | 0.98879 | 0.95559 | 0.93083 | 0.97494 | 0.97824 | 0.98244 | 0.98774 | 0.97827 | 0.74183 | 0.90448 | [10 empty] | 93 | 73523.9648 | 71057 | 0.96645 | 19 | Fixed | -1.893% | -104.4725 | 6197.2308 | [18 empty] | 1.2759 | 1 | [11 empty] | 40075 | 5827.3446 | 5798.2079 | 5769.2168 | 5740.3708 | 5711.6689 | 5683.1106 | 5654.695 | 0.99727 | [6 empty] | -132.8571 | 6256.4286 | -2.294% | -162.6429 | 6840 | -3.12% | 65316.7551 | 186870.9388 | 117.8776 | 2401 | 17994.3061 | 28657.6531 | 34808.898 | 1215.0204 | 15322.9031 | 83191.0408 | 137694.0051 | 635664.5102 | 56338.4133 | [10 empty] | 5.708% | 3% | 52.55% | 3.828% | 78.37%
94 | 57739 | SPS4 Monument SunE | 2012 | 2011 | IPP Non-CHP | c-Si | SunEdison | Tracker | 0 | NM | 32.682 | -103.3 | 10.8 | 10.1 | 2666.325 | Midland | 17.4 | 48.6675 | M | 1955.5 | 618 | 0.618 | 0.31603 | 2.919% | 0.68626 | 21885.1956 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 24234; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 24312; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 23198; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 22368; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 12616; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 16493; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 20382; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 20615; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 22474; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 21989; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 22266; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 22319; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 22858; Median age 14: 13 |  | 94 | 1.1073 | 1.1165 | 1.0707 | 1.0375 | 0.58814 | 0.77274 | 0.95975 | 0.9756 | 1.0689 | 1.0511 | 1.0697 | 1.0776 | 1.1092 | [10 empty] | 94 | 276126.8572 | 276124 | 0.99999 | 12 | Tracker | 0.01945% | 4.1319 | 21211.3846 | [18 empty] | 1.0693 | 1 | [11 empty] | 143603 | 21885.1956 | 21775.7696 | 21666.8908 | 21558.5563 | 21450.7635 | 21343.5097 | 21236.7922 | 0.95153 | [6 empty] | -1349.1429 | 25911.2857 | -6.367% | 379.5714 | 18047.5714 | 1.738% | 107677.7347 | 1207801 | 1779937.1633 | 3434667.9388 | 42896885.898 | 1751463.1837 | 15324987.9388 | 220095.0204 | 1020677.2245 | 21232.6531 | 1861.3061 | 80331.7551 | 15376 | [10 empty] | 10.76% | 2.7% | 25.1% | 15.02% | 17.97%
95 | 57438 | Solar Park Gainesville, LLC | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Fixed | 15 | FL | 29.7 | -82.338 | 2 | 1.6 | 1789.725 | Jacksonville | 20 | 44.7515 | M | 1682 | 735.6 | 0.524 | 0.43734 | 0.7995% | 0.90201 | 2863.56 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2862; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2740; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2673; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2327; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2756; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2487; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 2279; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 2273; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 1974; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 2033; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 1663; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 1468; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 1475; Median age 14: 13 |  | 95 | 0.99946 | 0.96166 | 0.94286 | 0.82494 | 0.98193 | 0.89054 | 0.82016 | 0.82211 | 0.71756 | 0.74272 | 0.6106 | 0.54171 | 0.54703 | [10 empty] | 95 | 36129.7124 | 29010 | 0.80294 | 67 | Fixed | -5.13% | -117.4835 | 3053.9231 | [18 empty] | 1.25 | 1 | [11 empty] | 18124 | 2863.56 | 2849.2422 | 2834.996 | 2820.821 | 2806.7169 | 2792.6833 | 2778.7199 | 0.91782 | [6 empty] | -77.5714 | 2899.4286 | -2.952% | -154.75 | 3428.2143 | -8.228% | 1611.449 | 18.3673 | 39.5102 | 68718.8776 | 59745.3265 | 2809 | 5995.1837 | 6853.4745 | 3777.8584 | 23190.9388 | 3964.5013 | 10653.1888 | 3426.4298 | [10 empty] | 5.429% | 2.8% | 51.58% | 5.441% | 51.46%
96 | 57497 | Stroud | 2012 | 2011 | Electric Utility | c-Si | PG&E | Fixed | 25 | CA | 36.531 | -120.107 | 24.6 | 20 | 2081.925 | Fresno | 17.4 | 44.3235 | M | 1910 | 578 | 0.634 | 0.30262 | 0% | 1 | 40972.284 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 43065; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 44933; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 42715; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 40966; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 38539; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 34751; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 37339; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 33509; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 33705; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 31997; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 29512; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 24471; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 21268; Median age 14: 13 |  | 96 | 1.0511 | 1.1022 | 1.053 | 1.015 | 0.95966 | 0.86968 | 0.93915 | 0.84705 | 0.85629 | 0.81698 | 0.75732 | 0.63111 | 0.55126 | [10 empty] | 96 | 516949.8239 | 456770 | 0.88359 | 46 | Fixed | -4.937% | -1778.6868 | 47586.9615 | [18 empty] | 1.23 | 1 | [11 empty] | 282308 | 40972.284 | 40767.4226 | 40563.5855 | 40360.7675 | 40158.9637 | 39958.1689 | 39758.378 | 0.99918 | [6 empty] | -1489.9286 | 46289.4286 | -3.627% | -2517.2143 | 55429.4286 | -8.319% | 3008490.25 | 2635520.3265 | 801664.4133 | 404859.5102 | 90472.0459 | 6754058.449 | 2187652.2908 | 3178070.2245 | 865830.25 | 3026605.7959 | 3139730.8622 | 565289.1633 | 2066816.9847 | [10 empty] | 4.231% | 3.6% | 85.09% | 3.735% | 96.39%
97 | 57745 | Vineland West | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | NJ | 39.462 | -75.07 | 4.8 | 3.7 | 1680.15 | Atlantic City | 11.7 | 35.637 | C | 1486 | 672 | 0.509 | 0.45222 | 0.7167% | 0.91169 | 6451.776 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 6744; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 6676; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 6631; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 6587; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 6387; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 6335; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 3724; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 3891; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 3716; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 3744; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 3704; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 3475; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 3317; Median age 14: 13 |  | 97 | 1.0453 | 1.04 | 1.0381 | 1.0364 | 1.01 | 1.0068 | 0.59483 | 0.62463 | 0.59953 | 0.60708 | 0.60362 | 0.56914 | 0.546 | [10 empty] | 97 | 81402.4541 | 64931 | 0.79765 | 68 | Fixed | -6.862% | -354.8901 | 7478.9231 | [18 empty] | 1.2973 | 1 | [11 empty] | 43084 | 6451.776 | 6419.5171 | 6387.4195 | 6355.4824 | 6323.705 | 6292.0865 | 6260.6261 | 0.96838 |  |  | 0.79765 | -6.862% |  | 0.96838 | -356.6429 | 7581.4286 | -5.631% | -73.75 | 4390.5 | -2.019% | 231154.9031 | 36918.8776 | 14280.25 | 186747.449 | 346668.6173 | 798214.6122 | 1852126.5765 | 8190.25 | 115.5625 | 8281 | 15562.5625 | 930.25 | 13167.5625 | [10 empty] | 10.41% | 3% | 28.83% | 11.43% | 26.24%
98 | 57660 | Vineland Mays Landing Solar | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | NJ | 39.4175 | -74.974 | 4.7 | 4 | 1935.825 | Atlantic City | 11.7 | 37.5375 | C | 1486 | 672 | 0.509 | 0.45222 | 1.66% | 0.80719 | 6914.7669 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 7245; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 6969; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 6760; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 7105; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 7030; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 6728; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 6353; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 6706; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 5959; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 5879; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 7103; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 6741; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 6820; Median age 14: 13 |  | 98 | 1.0478 | 1.0129 | 0.98747 | 1.0431 | 1.0373 | 0.99768 | 0.94681 | 1.0044 | 0.89704 | 0.88944 | 1.08 | 1.0301 | 1.0474 | [10 empty] | 98 | 87244.0387 | 87398 | 1.0018 | 11 | Tracker | -0.6647% | -44.8352 | 7036.7692 | [18 empty] | 1.175 | 1 | [11 empty] | 48190 | 6914.7669 | 6880.1931 | 6845.7921 | 6811.5631 | 6777.5053 | 6743.6178 | 6709.8997 | 1.0106 |  |  | 1.0018 | -0.6647% |  | 1.0106 | -103.1429 | 7296.8571 | -1.487% | 93.3929 | 5574.7857 | 1.435% | 2630.2245 | 14779.6122 | 51723.7551 | 48714.7959 | 61929.8776 | 2500 | 49220.5918 | 147510.8622 | 208229.2462 | 396540.0816 | 250893.6543 | 2070.25 | 967.6543 | [10 empty] | 4.59% | 3.4% | 74.08% | 2.642% | 128.7%
99 | 57699 | Webberville | 2012 | 2011 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | TX | 30.238 | -97.509 | 35 | 30 | 2337.6 | Austin | 20.3 | 49.124 | M | 1783.4 | 705 | 0.555 | 0.39531 | 4.29% | 0.57495 | 62180.16 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 60931; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 58978; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 57960; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 53729; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 44091; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 62444; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 57220; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 56483; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 57401; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 55044; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 62767; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 56430; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 56253; Median age 14: 13 |  | 99 | 0.97991 | 0.95327 | 0.94152 | 0.87718 | 0.72345 | 1.0297 | 0.94833 | 0.94082 | 0.96091 | 0.92608 | 1.0613 | 0.95897 | 0.96076 | [10 empty] | 99 | 784530.8981 | 739731 | 0.9429 | 26 | Tracker | 0.0292% | 16.6154 | 56786.0769 | [18 empty] | 1.1667 | 1 | [11 empty] | 395353 | 62180.16 | 61869.2592 | 61559.9129 | 61252.1133 | 60945.8528 | 60641.1235 | 60337.9179 | 0.92203 | [6 empty] | -645.3571 | 59060.4286 | -1.136% | 84.25 | 56528.6429 | 0.1469% | 6329896.5765 | 1459954.3673 | 698298.9847 | 7562500 | 137889661.2704 | 52645389.7959 | 7166711.4337 | 517885.8418 | 13020.4401 | 5415593.8776 | 28213170.4401 | 1231307.2704 | 1879347.2258 | [10 empty] | 7.722% | 2.9% | 37.55% | 9.784% | 29.64%
100 | 57499 | Westside Solar Station | 2012 | 2011 | Electric Utility | c-Si | PG&E | Fixed | 25 | CA | 36.378 | -120.125 | 18.5 | 15 | 2081.925 | Fresno | 17.4 | 44.3235 | M | 1910 | 578 | 0.634 | 0.30262 | 0% | 1 | 30812.49 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 32301; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 32642; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 32102; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 28713; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 30612; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 25383; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 28708; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 27663; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 9: 24389; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 10: 20840; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 11: 17699; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 12: 18529; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 13: 13870; Median age 14: 13 |  | 100 | 1.0483 | 1.0647 | 1.0523 | 0.94598 | 1.0136 | 0.8447 | 0.96015 | 0.92985 | 0.82392 | 0.70756 | 0.60394 | 0.63544 | 0.47805 | [10 empty] | 100 | 388763.079 | 333451 | 0.85772 | 54 | Fixed | -5.673% | -1497.5165 | 36132.6923 | [18 empty] | 1.2333 | 1 | [11 empty] | 210461 | 30812.49 | 30658.4276 | 30505.1354 | 30352.6097 | 30200.8467 | 30049.8425 | 29899.5932 | 0.9905 | [6 empty] | -956.6786 | 33892.5714 | -3.132% | -2481.1429 | 46482.5714 | -11.45% | 403088.9401 | 439284.9031 | 1165243.1441 | 1830222.449 | 2258472.2462 | 7670130.25 | 2286684.0319 | 1060017.3265 | 56033.6531 | 690798.449 | 2223081 | 3312920.0204 | 127959.5102 | [10 empty] | 5.244% | 3.6% | 68.64% | 5.037% | 71.47%
[27 empty] | 6.2391 21: y=mx+b equation to get p90obs/p50 by yr >>; 6.2391 22: -0.024653; 6.2391 23: 0.82513; Median age 14: avg>> | 0.61558 | p90stat/median | 0.78883 | 0.71657 | 0.70508 | 0.73187 | 0.7084 | 0.71818 | 0.75841 | 0.62712 | 0.56353 | 0.59733 | 0.62389 | 0.57403 | 0.55587 | 0.30639 | 0.3971 | 0.47668
[27 empty] | 6.2391 21: y=mx+b equation to get p90stat/p50 by yr >>; 6.2391 22: -0.025815; 6.2391 23: 0.86753; Median age 14: avg>> | 0.64811 | p90obs/median | 0.78854 | 0.74822 | 0.78075 | 0.81378 | 0.74634 | 0.8027 | 0.76858 | 0.68508 | 0.63357 | 0.54024 | 0.59828 | 0.60017 | 0.60306 | 0.18373 | 0.45199 | 0.6247
[52 empty] | Median | 0.95385 | 0.97112 | 0.96056 | 0.95053 | 0.95069 | 0.93482 | 0.91966 | 0.91175 | 0.87512 | 0.84431 | 0.8688 | 0.83999 | 0.7788 | 0.73854 | 0.60729 | 0.6143 | [12 empty] | median> | -2.33% | bar: 6.2391 22 to 6.2391 23
[27 empty] | 6.2391 22: For ex., enter yr# |  | Sys count | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 97 | 73 | 41 | 24 | 4 | 1 | 1 | 1 | 1 | 1 | 1 |  | 14987169.1151 | 13660673.45 | 0.91149 |  | average> | -3.111%
[27 empty] | 6.2391 22: 8 |  | Rank,p90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 66 | 37 | 22 | 4 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | avg PI > | 0.84068 |  |  | simple average degr rate if all systems are assumed to degrade linearly from year 1.
[27 empty] | 6.2391 22: The p90observed/p50 ratio is: |  | Line#, p90 | 53 | 25 | 37 | 25 | 37 | 65 | 16 | 97 | 76 | 10 | 85 | 65 | 72 | 42 | 35 | 31 | [9 empty] | stdev PI > | 0.14359
[27 empty] | 6.2391 22: 0.66102 |  | p90 (obs.rank) | 0.75215 | 0.72661 | 0.74996 | 0.77352 | 0.70954 | 0.75038 | 0.70683 | 0.62463 | 0.55445 | 0.45613 | 0.51978 | 0.50413 | 0.46966 | 0.13569 | 0.27449 | 0.38375 | [8 empty] | trkr only | trkr only | PI |  |  | There were 2-3 examples of small lifetime annual improvement, not degradation, mostly due to zero output in some early year
[27 empty] | 6.2391 22: The p90statistical/p50 ratio is: |  | Line # | Annual Rankings, seek to find the 90% percentile (i.e., boundary of worst 10%) | [23 empty] | 6076966.9329 | 5551588.45 | 0.91355 |  |  | -20.74% | this was the worst case degradation (Pacific Cruise Lines rooftop fixed-tilt)
[27 empty] | 6.2391 22: 0.62791 |  | 1 | 94 | 97 | 99 | 98 | 89 | 85 | 99 | 72 | 62 | 61 | 75 | 93 | 95 | 58 | 35 | 17 | [8 empty] | fixed only | fixed only
[52 empty] | 2 | 22 | 33 | 38 | 22 | 18 | 19 | 15 | 21 | 82 | 33 | 45 | 45 | 40 | 42 | 16 | 7 | [8 empty] | 8910202.1822 | 8109085 | 0.91009
[52 empty] | 3 | 75 | 80 | 72 | 70 | 67 | 72 | 72 | 98 | 96 | 1 | 53 | 53 | 51 | 41 | 14 | 13
[52 empty] | 4 | 65 | 32 | 23 | 14 | 46 | 21 | 11 | 8 | 6 | 16 | 2 | 6 | 7 | 2 | 3 | 6
[52 empty] | 5 | 98 | 95 | 51 | 52 | 61 | 53 | 97 | 61 | 69 | 92 | 64 | 77 | 91 | 63 | 38 | 23
[52 empty] | 6 | 60 | 73 | 64 | 65 | 68 | 69 | 59 | 65 | 52 | 47 | 13 | 17 | 39 | 22 | 7 | 3
[52 empty] | 7 | 61 | 11 | 91 | 96 | 17 | 11 | 27 | 25 | 23 | 20 | 47 | 12 | 48 | 38 | 34 | 4
[52 empty] | 8 | 93 | 46 | 40 | 99 | 54 | 30 | 43 | 49 | 31 | 1 | 44 | 32 | 55 | 37 | 13
[52 empty] | 9 | 67 | 49 | 65 | 33 | 97 | 86 | 63 | 39 | 61 | 69 | 85 | 76 | 89 | 67 | 29 | 21
[52 empty] | 10 | 99 | 94 | 95 | 89 | 95 | 97 | 94 | 74 | 77 | 90 | 93 | 95 | 95 | 69 | 39 | 24
[52 empty] | 11 | 76 | 36 | 52 | 32 | 38 | 52 | 24 | 15 | 33 | 54 | 27 | 35 | 25 | 17 | 11 | 2
[52 empty] | 12 | 84 | 57 | 82 | 88 | 84 | 78 | 82 | 76 | 66 | 64 | 79 | 58 | 56 | 40 | 15 | 11
[52 empty] | 13 | 100 | 93 | 54 | 62 | 79 | 58 | 61 | 52 | 58 | 81 | 92 | 86 | 84 | 50 | 28 | 19
[52 empty] | 14 | 81 | 78 | 68 | 76 | 59 | 67 | 54 | 55 | 40 | 58 | 65 | 65
[52 empty] | 15 | 95 | 98 | 15 | 27 | 37 | 44 | 22 | 28 | 21 | 26 | 15 | 44 | 75 | 49 | 27 | 16
[52 empty] | 16 | 1 | 2 | 3 | 8 | 1 | 5 | 90 | 81 | 89 | 98 | 76 | 51 | 20 | 8 | 2
[52 empty] | 17 | 78 | 85 | 100 | 82 | 82 | 80 | 91 | 71 | 67 | 42 | 71 | 38 | 80 | 53
[52 empty] | 18 | 1 | 58 | 1 | 58 | 39 | 46 | 17 | 23 | 35 | 28 | 37 | 15 | 12 | 7 | 4
[52 empty] | 19 | 69 | 71 | 57 | 91 | 58 | 61 | 67 | 1 | 63 | 80 | 55 | 59 | 63 | 62 | 24 | 9
[52 empty] | 20 | 6 | 9 | 4 | 9 | 24 | 6 | 7 | 12 | 10 | 17 | 46 | 27 | 41 | 36 | 20
[52 empty] | 21 | 30 | 37 | 7 | 16 | 10 | 16 | 9 | 10 | 12 | 10 | 11 | 22 | 11 | 12 | 8 | 1
[52 empty] | 22 | 73 | 40 | 66 | 36 | 64 | 96 | 88 | 82 | 47 | 56 | 62 | 66 | 64 | 23 | 10 | 8
[52 empty] | 23 | 72 | 81 | 1 | 72 | 73 | 83 | 30 | 95 | 98 | 87 | 78 | 62 | 52 | 28 | 23 | 18
[52 empty] | 24 | 46 | 96 | 49 | 38 | 9 | 33 | 18 | 42 | 57 | 82 | 41 | 40 | 45 | 59 | 32 | 10
[52 empty] | 25 | 86 | 90 | 85 | 90 | 99 | 84 | 77 | 79 | 76 | 67 | 69 | 78 | 74 | 57 | 39
[52 empty] | 26 | 41 | 84 | 42 | 47 | 65 | 63 | 34 | 57 | 65 | 46 | 43 | 52 | 31 | 26 | 17
[52 empty] | 27 | 40 | 54 | 36 | 39 | 80 | 74 | 1 | 27 | 16 | 45 | 42 | 41 | 65 | 35 | 25
[52 empty] | 28 | 32 | 24 | 50 | 41 | 50 | 50 | 47 | 51 | 50 | 38 | 50 | 47 | 35 | 25 | 6
[52 empty] | 29 | 87 | 89 | 96 | 97 | 96 | 98 | 98 | 96 | 95 | 94 | 95 | 72 | 90 | 70
[52 empty] | 30 | 38 | 70 | 47 | 44 | 30 | 48 | 46 | 1 | 70 | 65 | 73 | 79 | 47 | 31 | 36 | 14
[52 empty] | 31 | 64 | 66 | 48 | 74 | 81 | 77 | 83 | 1 | 85 | 53 | 81 | 60 | 69 | 65 | 30 | 22
[52 empty] | 32 | 91 | 26 | 35 | 42 | 72 | 25 | 35 | 88 | 64 | 88 | 34 | 57 | 59 | 64 | 19 | 12
[52 empty] | 33 | 68 | 76 | 70 | 40 | 15 | 17 | 23 | 54 | 49 | 34 | 25 | 24 | 1 | 29 | 5
[52 empty] | 34 | 43 | 59 | 55 | 45 | 62 | 59 | 58 | 94 | 87 | 50 | 94 | 63 | 66 | 48 | 18 | 20
[52 empty] | 35 | 71 | 63 | 74 | 51 | 53 | 68 | 60 | 91 | 53 | 52 | 51 | 74 | 42 | 56 | 37
[52 empty] | 36 | 28 | 20 | 25 | 1 | 31 | 3 | 19 | 66 | 9 | 66 | 38 | 56 | 13 | 13 | 9
[52 empty] | 37 | 92 | 91 | 90 | 94 | 90 | 99 | 89 | 86 | 72 | 83 | 82 | 91 | 83 | 60 | 33
[52 empty] | 38 | 23 | 62 | 41 | 59 | 71 | 57 | 74 | 97 | 94 | 89 | 35 | 54 | 62 | 43 | 31 | 15
[52 empty] | 39 | 97 | 92 | 92 | 95 | 88 | 81 | 68 | 85 | 81 | 96 | 98 | 68 | 68 | 46 | 26
[52 empty] | 40 | 7 | 53 | 67 | 73 | 76 | 60 | 56 | 62 | 54 | 57 | 57 | 48 | 58 | 32
[52 empty] | 41 | 50 | 64 | 63 | 67 | 60 | 65 | 50 | 47 | 41 | 31 | 48 | 34 | 38 | 19
[52 empty] | 42 | 55 | 34 | 19 | 25 | 32 | 55 | 28 | 32 | 43 | 36 | 89 | 49 | 70 | 66
[52 empty] | 43 | 54 | 47 | 43 | 87 | 93 | 88 | 66 | 83 | 92 | 99 | 68 | 4 | 17 | 9 | 1
[52 empty] | 44 | 20 | 19 | 31 | 50 | 56 | 37 | 42 | 22 | 26 | 21 | 18 | 25 | 27 | 39
[52 empty] | 45 | 96 | 87 | 86 | 2 | 92 | 94 | 93 | 84 | 80 | 73 | 77 | 71 | 73
[52 empty] | 46 | 74 | 43 | 61 | 55 | 74 | 64 | 92 | 93 | 73 | 75 | 70 | 89 | 76
[52 empty] | 47 | 52 | 99 | 98 | 43 | 42 | 39 | 5 | 24 | 48 | 55 | 52 | 88 | 72 | 52 | 22
[52 empty] | 48 | 21 | 39 | 84 | 68 | 21 | 32 | 53 | 78 | 78 | 93 | 96 | 97
[52 empty] | 49 | 63 | 22 | 27 | 37 | 19 | 7 | 41 | 69 | 11 | 19 | 20 | 67 | 34 | 70
[52 empty] | 50 | 9 | 12 | 9 | 3 | 2 | 26 | 8 | 5 | 4 | 4 | 1
[52 empty] | 51 | 16 | 17 | 22 | 24 | 26 | 10 | 6 | 7 | 3 | 6 | 9 | 23 | 15 | 70 | 39
[52 empty] | 52 | 82 | 23 | 29 | 80 | 45 | 43 | 75 | 73 | 91 | 71 | 80 | 94 | 85 | 61 | 39
[52 empty] | 53 | 90 | 56 | 59 | 81 | 55 | 36 | 69 | 50 | 75 | 24 | 28 | 50 | 43 | 14 | 39
[52 empty] | 54 | 11 | 44 | 33 | 31 | 51 | 35 | 25 | 64 | 44 | 62 | 59 | 37 | 53 | 44 | 39
[52 empty] | 55 | 42 | 1 | 17 | 28 | 12 | 8 | 3 | 48 | 7 | 13 | 17 | 7 | 30 | 21 | 39
[52 empty] | 56 | 27 | 14 | 18 | 18 | 5 | 18 | 21 | 44 | 8 | 14 | 10 | 13 | 4 | 5 | 39
[52 empty] | 57 | 59 | 61 | 93 | 60 | 41 | 12 | 29 | 30 | 28 | 12 | 74 | 28 | 19 | 3 | 39
[52 empty] | 58 | 70 | 77 | 81 | 83 | 91 | 89 | 85 | 100 | 68 | 39 | 49 | 80 | 60 | 70 | 39
[52 empty] | 59 | 85 | 86 | 89 | 46 | 52 | 56 | 73 | 59 | 83 | 85 | 100 | 70 | 92 | 68 | 39
[52 empty] | 60 | 80 | 75 | 79 | 71 | 66 | 41 | 65 | 56 | 37 | 22 | 39 | 16 | 46 | 18 | 39
[52 empty] | 61 | 24 | 82 | 32 | 30 | 100 | 99 | 100 | 99 | 98 | 97 | 97 | 99 | 95 | 70 | 39
[52 empty] | 62 | 18 | 3 | 5 | 6 | 57 | 2 | 62 | 80 | 2 | 7 | 33 | 42 | 33 | 20 | 39
[52 empty] | 63 | 56 | 45 | 73 | 93 | 75 | 23 | 45 | 58 | 36 | 63 | 63 | 83 | 78 | 45 | 39
[52 empty] | 64 | 39 | 48 | 44 | 15 | 11 | 42 | 13 | 37 | 17 | 25 | 29 | 85 | 50 | 34 | 21
[52 empty] | 65 | 58 | 79 | 75 | 77 | 86 | 90 | 86 | 92 | 93 | 95 | 91 | 90 | 86 | 55 | 39
[52 empty] | 66 | 8 | 18 | 16 | 5 | 29 | 31 | 4 | 9 | 59 | 29 | 24 | 61 | 61 | 24 | 39
[52 empty] | 67 | 62 | 25 | 26 | 57 | 44 | 27 | 20 | 38 | 30 | 11 | 61 | 3 | 6 | 4 | 39
[52 empty] | 68 | 10 | 16 | 14 | 20 | 16 | 4 | 51 | 11 | 18 | 44 | 19 | 39 | 49 | 51 | 39
[52 empty] | 69 | 51 | 52 | 97 | 49 | 40 | 29 | 38 | 16 | 25 | 23 | 30 | 31 | 29 | 11 | 39
[52 empty] | 70 | 47 | 69 | 69 | 79 | 69 | 34 | 64 | 63 | 45 | 60 | 54 | 55 | 57 | 47 | 39
[52 empty] | 71 | 53 | 67 | 71 | 53 | 35 | 54 | 57 | 34 | 22 | 74 | 23 | 21 | 18 | 70 | 39
[52 empty] | 72 | 83 | 83 | 87 | 92 | 98 | 82 | 70 | 89 | 71 | 91 | 99 | 98 | 88 | 70 | 39
[52 empty] | 73 | 44 | 31 | 78 | 84 | 6 | 92 | 55 | 20 | 88 | 72 | 12 | 2 | 5 | 6 | 39
[52 empty] | 74 | 49 | 10 | 46 | 29 | 22 | 24 | 37 | 46 | 46 | 51 | 31 | 36 | 54 | 27 | 12
[52 empty] | 75 | 79 | 13 | 21 | 11 | 3 | 1 | 10 | 31 | 14 | 8 | 66 | 1 | 3 | 1 | 39
[52 empty] | 76 | 37 | 41 | 37 | 35 | 25 | 45 | 33 | 40 | 90 | 84 | 83 | 96 | 93 | 70 | 39
[52 empty] | 77 | 31 | 8 | 88 | 4 | 85 | 79 | 71 | 4 | 32 | 40 | 58 | 99 | 95 | 70 | 39
[52 empty] | 78 | 33 | 51 | 76 | 63 | 33 | 47 | 52 | 19 | 24 | 30 | 7 | 29 | 16 | 70 | 39
[52 empty] | 79 | 77 | 74 | 83 | 69 | 78 | 95 | 76 | 67 | 97 | 76 | 72 | 73 | 71 | 70 | 39
[52 empty] | 80 | 4 | 27 | 24 | 21 | 8 | 14 | 2 | 14 | 5 | 3 | 4 | 9 | 10 | 70 | 39
[52 empty] | 81 | 48 | 29 | 11 | 48 | 49 | 73 | 84 | 77 | 38 | 48 | 36 | 33 | 26 | 30 | 39
[52 empty] | 82 | 45 | 28 | 10 | 54 | 70 | 70 | 95 | 53 | 34 | 49 | 32 | 43 | 37 | 16 | 39
[52 empty] | 83 | 25 | 42 | 56 | 61 | 34 | 38 | 36 | 35 | 13 | 27 | 26 | 18 | 14 | 70 | 39
[52 empty] | 84 | 89 | 100 | 80 | 17 | 43 | 20 | 14 | 18 | 19 | 41 | 40 | 14 | 23 | 10 | 39
[52 empty] | 85 | 88 | 88 | 94 | 86 | 83 | 91 | 87 | 87 | 79 | 77 | 90 | 92 | 94 | 70 | 39
[52 empty] | 86 | 34 | 72 | 53 | 26 | 27 | 62 | 49 | 33 | 29 | 37 | 21 | 46 | 36 | 70 | 39
[52 empty] | 87 | 35 | 65 | 58 | 64 | 77 | 93 | 80 | 60 | 51 | 35 | 60 | 30 | 32 | 70 | 39
[52 empty] | 88 | 3 | 7 | 6 | 7 | 4 | 15 | 16 | 6 | 15 | 5 | 8 | 8 | 44 | 33 | 39
[52 empty] | 89 | 19 | 50 | 45 | 75 | 13 | 40 | 12 | 43 | 55 | 68 | 84 | 75 | 77 | 70 | 39
[52 empty] | 90 | 57 | 38 | 28 | 19 | 28 | 49 | 48 | 45 | 39 | 15 | 14 | 11 | 21 | 70 | 39
[52 empty] | 91 | 66 | 68 | 77 | 99 | 63 | 75 | 79 | 75 | 84 | 78 | 56 | 69 | 67 | 54 | 39
[52 empty] | 92 | 12 | 35 | 34 | 66 | 7 | 9 | 81 | 13 | 98 | 99 | 16 | 20 | 24 | 70 | 39
[52 empty] | 93 | 26 | 5 | 30 | 34 | 48 | 51 | 26 | 26 | 20 | 18 | 22 | 64 | 28 | 70 | 39
[52 empty] | 94 | 5 | 4 | 8 | 12 | 94 | 87 | 32 | 29 | 1 | 9 | 5 | 5 | 2 | 70 | 39
[52 empty] | 95 | 29 | 55 | 60 | 85 | 36 | 66 | 78 | 70 | 74 | 70 | 86 | 87 | 81 | 70 | 39
[52 empty] | 96 | 13 | 6 | 12 | 23 | 47 | 71 | 44 | 68 | 56 | 59 | 67 | 82 | 79 | 70 | 39
[52 empty] | 97 | 17 | 21 | 20 | 13 | 23 | 22 | 96 | 90 | 86 | 86 | 88 | 84 | 82 | 70 | 39
[52 empty] | 98 | 15 | 30 | 39 | 10 | 14 | 28 | 40 | 17 | 42 | 43 | 3 | 10 | 9 | 70 | 39
[52 empty] | 99 | 36 | 60 | 62 | 78 | 87 | 13 | 39 | 36 | 27 | 32 | 6 | 26 | 22 | 70 | 39
[52 empty] | 100 | 14 | 15 | 13 | 56 | 20 | 76 | 31 | 41 | 60 | 79 | 87 | 81 | 87 | 70 | 39
[52 empty] | Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
[52 empty] | Rank,p10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 4 | 2
[52 empty] | Line#, p10 | 68 | 74 | 82 | 98 | 21 | 51 | 75 | 21 | 20 | 21 | 56 | 98 | 80 | 18 | 18 | 11
[52 empty] | p10 (obs.rank) | 1.0783 | 1.0757 | 1.0575 | 1.0431 | 1.0469 | 1.0401 | 1.0251 | 1.0482 | 1.011 | 1.0413 | 1.032 | 1.0301 | 1.0341 | 1.0415 | 0.99573 | 0.89977
Note on BR1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rate evaluated at midpoint of interval (4 yrs)
Note on BW1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rate evaluated at midpoint of interval (4.5 yrs from Yr 7)
Note on N7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on visual module count and nameplate module W
Note on G8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Nellis’s biggest share is 5 MW SunPower, but it also has nearly as much Suntech and 2 MW each of Sanyo HIT bifacial and Evergreen ribbon Si.
Note on AA8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual override based on Wikipedia Reply: Should be 14.2x3147x0.76=33,962 (6% higher)
Note on AA13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual override based on BEW IE report, with a shitty 0.68 PR expected Reply: Should be 1.173x1937x0.8=1,818 (17% higher)
Note on E70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inserted EPRI report data for 2009 and replaced 2010 EIA (rounded bogus?) number with EPRI number.
Note on G70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 26% of this is First Solar 72.5 W modules
Note on J92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2-axis tracker

## DetailOfP50
Detailed look at the role of weather variability and system output variability for a few of the "most median" representative older systems | [13 empty] | 45.69%
|  |  |  | User degr entry from main PlantData tab | Add'l degr here | << be careful not to impose add'l degr if |  |  |  |  | Avg of 5 |  |  | Explainable
|  |  |  | 0.5% | 0.5% | entry on PlantData tab has already been chosen |  |  |  |  | 0.90712 |  |  | part of |  |  | Predicted PI coefficients, straight line | [21 empty] | Estimated PI by year
|  | lifetime |  |  | p50 Yr1 exp. |  | Normal POA | LTAvg | Structure | Expected | Degr.Adj | 7-yr | lifetime | lifetime | 7-yr | post-7 | 1st 7 years |  | Yr7 onward |  | Yrs of data | Estimated PI, based on actual MWh by year and lt-avg POA, size, and expected PR | [16 empty] | Best-fit
PI rank | Name | variability | State | MWp | MWh | TMY2 | Variability | POA | Type | PR | Life PI | variability | variability | variability | degr. | degr. | slope | intercept | slope | intercept |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
48 | Cotton Center Solar Hybrid | 5.14% | AZ | 21 | 46635.12 | Phoenix | 3.6% | 2922 | Tracker | 0.76 | 0.90913 | 4.913% | 5.14% | 70.04% | -3.761% | -8.577% | -0.03447 | 1.0372 | -0.099079 | 1.7992 | 13 | 0.99255 | 0.94797 | 0.9573 | 0.94811 | 0.87252 | 0.73669 | 0.83995 | 0.90105 | 0.91027 | 0.96142 | 0.82731 | 0.98775 | 0.9562 | 0 | 0 |  |  | 1.0027 | 0.96824 | 0.93377 | 0.8993 | 0.86483 | 0.83036 | 0.95077 | 1.0066 | 0.90749 | 0.80841 | 0.70933 | 0.61025 | 0.51117 | 0.41209 | 0.31301
49 | CSU Fresno MMA | 17.55% | CA | 1.173 | 1547 | Fresno | 3% | 1937.286 | Fixed | 0.8 | 0.91633 | 16.47% | 17.55% | 17.1% | 1.809% | -2.748% | 0.016724 | 0.86604 | -0.027938 | 1.2542 | 17 | 0.93447 | 1.0833 | 0.74248 | 0.65513 | 1.0496 | 1.0656 | 0.99997 | 1.0191 | 1.0146 | 1.0298 | 0.92698 | 1.0745 | 0.83978 | 0.7818 |  |  |  | 0.88277 | 0.89949 | 0.91622 | 0.93294 | 0.94966 | 0.96639 | 1.0209 | 1.0307 | 1.0027 | 0.97478 | 0.94685 | 0.91891 | 0.89097 | 0.86303
50 | Albuquerque Solar Energy Center | 22.71% | NM | 2.4 | 4418.064 | Albuquerque | 3.6% | 2301.075 | Fixed | 0.8 | 0.90876 | 34.22% | 22.71% | 15.85% | 14.11% | 0.1221% | 0.10807 | 0.38774 | 0.0012348 | 1.0027 | 14 | 0.76787 | 0 | 0.86005 | 1.0425 | 0.98848 | 1.0426 | 1.0386 | 1.0418 | 1.026 | 0.94194 | 0.94039 | 1.0636 | 1.0196 | 1.0534 |  |  |  | 0.49581 | 0.60388 | 0.71194 | 0.82001 | 0.92807 | 1.0361 | 1.0778 | 1.0126 | 1.0138 | 1.015 | 1.0163 | 1.0175 | 1.0187 | 1.02
51 | Blue Wing | 4.716% | TX | 16.7 | 26155.4064 | San Antonio | 2.4% | 1957.74 | Fixed | 0.8 | 0.90455 | 5.009% | 4.716% | 50.89% | -2.476% | -8.853% | -0.02379 | 1.0443 | -0.10009 | 1.8311 | 14 | 1.0977 | 0.97535 | 0.92632 | 0.91405 | 0.8765 | 0.93422 | 0.91969 | 0.89611 | 0.9019 | 0.8575 | 0.84089 | 0.9124 | 0.76891 | 0.83307 | 0 | 0 | 0 | 1.0205 | 0.9967 | 0.97291 | 0.94912 | 0.92533 | 0.90154 | 1.0041 | 1.0304 | 0.9303 | 0.83021 | 0.73013 | 0.63004 | 0.52996 | 0.42987 | 0.32979 | 0.2297 | 0.12961
52 | Five Points Solar Station | 4.829% | CA | 17.6 | 29313.504 | Fresno | 3.6% | 2081.925 | Fixed | 0.8 | 0.89683 | 4.841% | 4.829% | 74.56% | 0.5884% | -6.834% | 0.0058578 | 0.97501 | -0.072854 | 1.5396 | 13 | 1.0242 | 0.97891 | 0.98741 | 0.89769 | 1.0622 | 0.99631 | 1.0423 | 0.9615 | 0.89452 | 0.78402 | 0.6799 | 0.72066 | 0.59446 |  |  |  |  | 0.98087 | 0.98673 | 0.99259 | 0.99845 | 1.0043 | 1.0102 | 1.0228 | 0.95677 | 0.88391 | 0.81106 | 0.7382 | 0.66535 | 0.59249

## DetailOfUASTP94thRank
Detailed look at the role of weather variability and system output variability for a few of the "most median" representative older systems | [13 empty] | 10.64%
|  |  |  | User degr entry from main PlantData tab | Add'l degr here | << be careful not to impose add'l degr if |  |  |  |  | Avg of 5 |  |  | Explainable
|  |  |  | 0.5% | 0.5% | entry on PlantData tab has already been chosen |  |  |  |  | 0.62019 |  |  | part of |  |  | Predicted PI coefficients, straight line | [21 empty] | Estimated PI by year
|  | lifetime |  |  | p50 Yr1 exp. |  | Normal POA | LTAvg | Structure | Expected | Degr.Adj | 7-yr | lifetime | lifetime | 7-yr | post-7 | 1st 7 years |  | Yr7 onward |  | Yrs of data | Estimated PI, based on actual MWh by year and lt-avg POA, size, and expected PR | [16 empty] | Best-fit
PI rank | Name | variability | State | MWp | MWh | TMY2 | Variability | POA | Type | PR | Life PI | variability | variability | variability | degr. | degr. | slope | intercept | slope | intercept |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
94 | UASTP I | 28.19% | AZ | 1.6 | 3597.5664 | Tucson | 3% | 2958.525 | Tracker | 0.76 | 0.62019 | 19.66% | 28.19% | 10.64% | -1.627% | -12.27% | -0.012561 | 0.81579 | -0.10713 | 1.5694 | 13 | 0.84658 | 0.87003 | 0.79066 | 0.73229 | 0.40667 | 0.82564 | 0.88693 | 0.65852 | 0.78019 | 0.46936 | 0.098575 | 0.12539 | 0.50003 | 0 | 0 |  |  | 0.80322 | 0.79066 | 0.7781 | 0.76554 | 0.75298 | 0.74042 | 0.77368 | 0.71238 | 0.60525 | 0.49813 | 0.391 | 0.28387 | 0.17675 | 0.069621 | -0.037505

## Newer25
25 system summary from 2018 start dates | [34 empty] | Top 12 states w/more than 1% (8 more states had 1 system apiece) | [9 empty] | Tracker | Fixed |  |  | 0.91716 | 0.8352 | 0.99553 | 0.93591 | PI, by year, with user's degradation allowance included as a user input variable (try 0% degr to see a fanning cloud of degrading outputs) | [14 empty] | ann. p50 SLD degr, yr1-7> | -0.4446% | -0.0040882 | 0.93578 | [6 empty] | min PI | 0.58516 | avg PI | 0.87033 | [42 empty] | 5.1%
data w/eqn. | just data | < data entry color key | [10 empty] | MWp | 168.6 |  | Top100 calcs, wtd by energy | [6 empty] | avg> | 3.081% | 71.71% |  | w/o degr | w/degr | MWh-wtd PI |  | smallest | 1.2 | MWp |  | CA | 2% | NC | 2% | FL | 1% | MA | 2% |  |  | %,PI,MWp | %,PI,MWp |  |  |  | ann. p90 expon degr, Yr1-Yr7 > | -8.284% | p90 (statistical) | 0.75144 | 0.77813 | 0.58544 | 0.56114 | 0.61381 | 0.44742 | 0.47727 | [18 empty] | median PI | 0.88714 | p90(1.28σ) | 0.70384 | -3.014% | <avg degr | [39 empty] | Median | Median | Median
| Expected PR | Fixed | 0.8 |  | Fleet median degradation, 1st 7 yrs |  | -0.4446% |  | Expctd Degr | 0% |  |  | MW,ac | 134.5 |  | 1624279 | MWh,act. | [5 empty] | median> | 2.293% | 74.23% |  | 1624279 |  | 88.31% |  | average | 6.744 | MWp |  | NJ | 1% | PA | 0% | NM | 1% | HI | 0% |  |  | 32% | 68% | [5 empty] | avg | 0.90889 | 0.9174 | 0.86134 | 0.8466 | 0.85535 | 0.80481 | 0.80834 | 0.92051 | [17 empty] | max PI | 1.0607 | p90(rank) | 0.67498 | -0.4658% | <median degr | [19 empty] | 1 | Most common |  | # at mode | 18 | [15 empty] | 6.236% | 3.2% | 51.57% | 1 | 1 | 18 | 18
| (user input) | Tracker | 0.76 | [5 empty] | MedianPI> | 0.88714 | (unwghtd) |  | ILR | 1.2535 |  | 1839307.8595 | MWh,exp. | eqn uses PVsyst | T,mod zones |  |  |  |  | CCC-based | estim. |  | 1839307.8595 | 1839307.8595 | 88.31% |  | largest | 71.4 | MWp |  | CO | 1% | AZ | 1% | NV | 0% | TX | 1% |  |  | 0.90211 | 0.85537 |  |  |  | ann. p50 expon degr, Yr1-Yr7 > | -0.4469% | Median | 0.92369 | 0.92822 | 0.93725 | 0.90083 | 0.93953 | 0.90864 | 0.89783 | 0.92051 | [16 empty] | Lifetime expected energy over number of years reported in the EIA database | [7 empty] | 5 new states in Top 25 highlighted in italics |  |  |  |  | Temp. Zone (>50,>40,<40) |  |  |  | System Size Differentiator |  |  |  | Ownership Differentiator |  |  |  |  | Delay Differentiator: years between start-up & full ops |  |  |  |  | Developer Differentiator |  |  |  |  | Module type differentiator |  | Inter-annual variability (IAV) analysis of generation and insolation (to the right) | [8 empty] | orientation |  | Median PI | Median Degr | Median PI | Median Degr
|  |  | 2019 | 18 | [8 empty] | 2.7 |  | 1888.7891 | 88.31% | < Fleet PI, wtd. | at 10 cities | H>50, M>40, | 1571.96 |  |  | 0.44733 | Corr'n. | Visible |  | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right | [17 empty] | 14.9625 | 2.8765 |  |  |  | Median age |  | stdev | 0.12301 | 0.1088 | 0.21554 | 0.22302 | 0.18871 | 0.27922 | 0.25865 | [17 empty] | This term uses the economics formula F/A, uniform series compound amount factor | [7 empty] | Average PI and degradation by state |  |  |  |  | Average PI and SLD degr by temperature | [7 empty] | CHP=Combined Heat & Power |  |  |  | 1.3333 | 1.04 | average | 0 | < min, # > | 3 | [5 empty] | (First Solar was sometimes used by |  | Squared deviation from straight-line fit, by year | [8 empty] | specific |  | 0.89112 | -0.4658% | 0.9032 | -0.1976%
Line# | EIA# | Name | 1st full yr | 1st kWh | Sector | Module type | Developer | (F)ix,(T)rkr | Slope/Tilt | State | Lat | Long | MWp | MWac | POA (by eqn.) | TMY2 Source | Annual T,air | Estim. Tmod | and C<40 | GHI | DHI | Kt | DF | Est.Clip | Degr Frac. | p50,Yr1 MWh | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 6 |  | Line # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Line # | Expected | Actual | Lifetime PI | Percentile Rank | Type | Lifetime Degr | Linest slope | Linest Int. | State | # systems | PI | Degr |  | Type | # systems | PI | SLD Degr | Size | PI | SLD | % of systems | Type | PI | SLD | # systems | ILR | 0.53852 | stdev | 2 | < max, # > | 4 | Name | Number | MWp | Avg PI | Avg SLD | developers other than FS) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | RMS variability | TMY2 variability | % explained variability | Hot | Hot | Cold | Cold
1 | 61345 | WyEast Solar | 2019 | 2018 | IPP Non-CHP | c-Si | Avangrid | Tracker | 0 | OR | 45.5846 | -120.5999 | 13 | 10 | 1983.515 | WyEast (Meteonorm) | 11.4 | 37.592 | C | 1510 | 526 | 0.562 | 0.34834 | 1.271% | 0.84774 | 19597.1278 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 18826; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 21768; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 22800; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 18385; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 19550; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 21091; Median age 6: 6 |  | 1 | 0.96065 | 1.1108 | 1.15 | 0.93815 | 0.9976 | 1.0762 | [17 empty] | 1 | 117582.7669 | 122420 | 1.0411 | 6 | Tracker | 0.03585% | 7.3143 | 20377.7333 | CA | 2 | 0.83205 | -16.08% |  | H | 1 | 0.89112 | -0.4658% | >5 MW,ac | 0.89857 | -0.3133% | 16 | Commercial CHP | #DIV/0! | #DIV/0! | 0 | 1.3 | 1 |  |  |  |  | Avangrid | 1 | 13 | 1.0411 | 0.00035855 | CdSCdTe | 1 | 2430629.4785 | 1892380.1691 | 5761554.3906 | 4088445.4858 | 747022.7215 | 448070.8594 |  |  | 7.844% | 3.9% | 49.72% |  |  | 1.0411 | 0.03585%
2 | 61656 | Grange Hall Solar | 2019 | 2018 | Electric Utility | CdSCdTe | Other utility | Tracker | 0 | FL | 27.6813 | -82.205 | 71.4 | 61.1 | 2301.075 | Tampa | 22.4 | 50.9525 | H | 1790 | 745 | 0.545 | 0.4162 | 4.597% | 0.55016 | 124865.5338 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 105555; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 118872; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 122960; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 112045; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 95572; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 104411; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 119476; Median age 6: 7 |  | 2 | 0.84535 | 0.952 | 0.98474 | 0.89733 | 0.7654 | 0.83619 | 0.95684 | [16 empty] | 2 | 874058.7366 | 778891 | 0.89112 | 46 | Tracker | -0.4658% | -519.5357 | 113348.2857 | NJ | 1 | 0.58516 | -20.57% |  | M | 6 | 0.84292 | -1.324% | <5 MW,ac | 0.86495 | -3.529% | 84 | Commercial Non-CHP | #DIV/0! | #DIV/0! | 0 | 1.1686 | 1 |  |  |  |  | Duke | 0 | 0 |  |  | c-Si | 23 | 52907439.0625 | 43070156.3316 | 124776080.8176 | 600403.5918 | 230390114.7972 | 33873231.4337 | 95344762.787 |  | 8.187% | 4.8% | 58.63% | 0.89112 | -0.4658%
3 | 61333 | Oak Hill Solar Array | 2019 | 2018 | Electric Utility | c-Si | Other utility | Fixed | 25 | IN | 37.99 | -87.53 | 2.7 | 2 | 1716.675 | Evansville | 13.2 | 37.4085 | C | 1534 | 703 | 0.516 | 0.45828 | 2.286% | 0.74292 | 3708.018 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3625; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3422; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3491; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3589; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3368; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 3336; Median age 6: 6 |  | 3 | 0.97761 | 0.92286 | 0.94147 | 0.9679 | 0.9083 | 0.89967 | [17 empty] | 3 | 22248.108 | 20831 | 0.9363 | 38 | Fixed | -1.234% | -43.1143 | 3622.7333 | CO | 1 | 0.96267 | -0.6253% |  | C | 18 | 0.87831 | -3.719% | All | 0.87033 | -3.014% | 100 | All Commercial | #DIV/0! | #DIV/0! | 0 | 1.35 | 1 |  |  |  |  | First Solar | 0 | 0 |  |  | HIT | 0 | 2059.4308 | 13111.3405 | 5.7144 | 19244.2953 | 1533.6548 | 786.6689 |  |  | 2.254% | 3.7% | 164.2% |  |  | 0.9363 | -1.234%
4 | 62558 | Kearsarge SKSC2 LLC | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | RI | 41.4983 | -71.5334 | 4.6 | 3.1 | 1643.625 | Providence | 10.2 | 33.8655 | C | 1424 | 674 | 0.502 | 0.47331 | 3.987% | 0.59556 | 6048.54 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 5587; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 6046; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 5820; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 5805; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 5713; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 5704; Median age 6: 6 |  | 4 | 0.92369 | 0.99958 | 0.96222 | 0.95974 | 0.94453 | 0.94304 | [17 empty] | 4 | 36291.24 | 34675 | 0.95546 | 30 | Fixed | -0.2119% | -12.2571 | 5822.0667 | NC | 2 | 0.86481 | -0.3789% |  | All | 25 | 0.87033 | -3.014% |  |  |  |  | Electric Utility | 0.89872 | -0.5788% | 3 | 1.4839 | 1 |  |  |  |  | MMA | 0 | 0 |  |  | Si_IBT | 0 | 49644.0839 | 61726.2194 | 1204.4205 | 1021.5634 | 2283.0194 | 1982.3696 |  |  | 2.425% | 3.8% | 156.7% |  |  | 0.95546 | -0.2119%
5 | 61557 | Facebook 2 Solar Energy Center | 2018 | 2018 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | NM | 35.08 | -108.865 | 12.5 | 10 | 2848.95 | Albuquerque | 13.4 | 46.025 | M | 2034 | 528 | 0.662 | 0.25959 | 8.123% | 0.34785 | 27065.025 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 24949; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 24181; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 25896; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 27675; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 27823; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 27059; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 28052; Median age 6: 7 |  | 5 | 0.92182 | 0.89344 | 0.95681 | 1.0225 | 1.028 | 0.99978 | 1.0365 | [16 empty] | 5 | 189455.175 | 185635 | 0.97984 | 22 | Tracker | 2.315% | 606.8571 | 24091.8571 | PA | 0 | [11 empty] | Industrial Non-CHP | #DIV/0! | #DIV/0! | 0 | 1.25 | 0 |  |  |  |  | NextEra | 0 | 0 |  |  | Unknown | 1 | 62642.9388 | 1264660.898 | 269.898 | 1335675.5102 | 485609.8776 | 454276 | 82861.7347 |  | 2.736% | 4.3% | 157.1%
6 | 62075 | Pima Community College | 2018 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 5 | AZ | 32.1665 | -110.8167 | 1.4 | 1.1 | 2191.5 | Tucson | 20.2 | 47.938 | M | 2082 | 544 | 0.658 | 0.26129 | 0.5051% | 0.93644 | 2454.48 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2798; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1702; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1192; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1201; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1512; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2404; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 788; Median age 6: 7 |  | 6 | 1.14 | 0.69343 | 0.48564 | 0.48931 | 0.61602 | 0.97943 | 0.32105 | [16 empty] | 6 | 17181.36 | 11597 | 0.67498 | 90 | Fixed | -8.871% | -153.7857 | 2271.8571 | AZ | 1 | 0.67498 | -8.871% | [9 empty] | IPP Non-CHP | 0.86646 | -3.346% | 22 | 1.2727 | 0 |  |  |  |  | NRG | 0 | 0 |  |  |  | 25 | 462302.8622 | 68793.7959 | 382542.25 | 207675.5102 | 82.2908 | 1112723.5918 | 165939.8418 |  | 35.34% | 2% | 5.659%
7 | 61983 | Cottage Grove Project CSG | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | MN | 44.7907 | -92.8727 | 6.4 | 4.9 | 1680.15 | Minneapolis | 7.2 | 31.137 | C | 1424 | 637 | 0.525 | 0.44733 | 0.7035% | 0.9126 | 8602.368 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 6682; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 7217; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 6364; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 6234; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 7051; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 6932; Median age 6: 6 |  | 7 | 0.77676 | 0.83896 | 0.7398 | 0.72468 | 0.81966 | 0.80582 | [17 empty] | 7 | 51614.208 | 40480 | 0.78428 | 74 | Fixed | 0.2638% | 17.7714 | 6684.4667 | FL | 1 | 0.89112 | -0.4658% | [9 empty] | All | 0.87033 | -3.014% | 25 | 1.3061 | 1 |  |  |  |  | Other utility | 3 | 79.1 | 0.89872 | -0.0057875 |  |  | 409.5805 | 246999.5334 | 139712.2004 | 272016.8861 | 77104.0668 | 19854.1519 |  |  | 5.262% | 3.8% | 72.22% |  |  | 0.78428 | 0.2638%
8 | 61506 | Krause CSG | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | MN | 44.7956 | -95.201 | 1.4 | 1 | 1680.15 | Saint Cloud | 5.3 | 29.237 | C | 1388 | 635 | 0.511 | 0.45749 | 2.605% | 0.71273 | 1881.768 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1749; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1522; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1877; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1523; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1906; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1802; Median age 6: 6 |  | 8 | 0.92945 | 0.80881 | 0.99747 | 0.80935 | 1.0129 | 0.95761 | [17 empty] | 8 | 11290.608 | 10379 | 0.91926 | 42 | Fixed | 1.771% | 30.3714 | 1623.5333 | NM | 1 | 0.97984 | 2.315% | [13 empty] | 1.4 | 1 |  |  |  |  | PG&E | 0 | 0 |  |  |  |  | 9043.1043 | 26333.562 | 26358.2956 | 49292.4575 | 17058.8477 | 14.1519 |  |  | 8.447% | 3.8% | 44.99% |  |  | 0.91926 | 1.771%
9 | 61504 | RJC I CSG | 2020 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | MN | 44.1251 | -93.285 | 1.4 | 1 | 1643.625 | Rochester | 6.4 | 30.0655 | C | 1388 | 654 | 0.504 | 0.47118 | 2.546% | 0.71819 | 1840.86 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1810; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1931; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1833; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1873; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1833; Median age 6: 5 |  | 9 | 0.98324 | 1.049 | 0.99573 | 1.0175 | 0.99573 | [18 empty] | 9 | 9204.3 | 9280 | 1.0082 | 10 | Fixed | -0.06463% | -1.2 | 1859.6 | NV | 0 | [15 empty] | 1.4 | 2 |  |  |  |  | SunEdison | 0 | 0 |  |  |  |  | 2342.56 | 5446.44 | 529 | 331.24 | 424.36 |  |  |  | 2.295% | 3.8% | 165.6% |  |  | 1.0082 | -0.06463%
10 | 62048 | USS Dubhe Solar CSG | 2020 | 2018 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | MN | 45.493 | -92.9044 | 1.4 | 1 | 1935.825 | Minneapolis | 7.2 | 33.0375 | C | 1424 | 637 | 0.525 | 0.44733 | 5.829% | 0.46869 | 2059.7178 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2094; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2041; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2165; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2015; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1985; Median age 6: 5 |  | 10 | 1.0166 | 0.99091 | 1.0511 | 0.97829 | 0.96372 | [18 empty] | 10 | 10298.589 | 10300 | 1.0001 | 14 | Tracker | -1.177% | -24.4 | 2133.2 | MA | 2 | 0.86727 | -0.7377% | [13 empty] | 1.4 | 2 |  |  |  |  | SunPower | 0 | 0 |  |  |  |  | 219.04 | 1883.56 | 11025 | 424.36 | 686.44 |  |  |  | 2.59% | 4.6% | 177.6% |  |  | 1.0001 | -1.177%
11 | 61627 | Waterville CSG Solar Holdings LLC | 2018 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | MN | 44.1971 | -93.5712 | 6.6 | 5 | 1680.15 | Minneapolis | 7.2 | 31.137 | C | 1424 | 637 | 0.525 | 0.44733 | 0.9353% | 0.88551 | 8871.192 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 7043; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 6618; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 7945; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 6781; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 6560; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 8170; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 8264; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 8: 8166; Median age 6: 8 |  | 11 | 0.79392 | 0.74601 | 0.8956 | 0.76438 | 0.73947 | 0.92096 | 0.93155 | 0.92051 | [15 empty] | 11 | 70969.536 | 59547 | 0.83905 | 66 | Fixed | 2.682% | 196.9643 | 6557.0357 | HI | 0 | [15 empty] | 1.32 | 0 |  |  |  |  | Unknown | 21 | 76.5 | 0.85814 | -0.035075 |  |  | 83521 | 110865.2156 | 635322.8622 | 317975.1543 | 964043.449 | 185914.9605 | 107724.6173 | 1105.5625 | 7.368% | 3.8% | 51.57% |  |  | 0.83905 | 2.682%
12 | 61882 | Copperfield | 2019 | 2018 | IPP Non-CHP | Unknown | Unknown | Tracker | 0 | NC | 35.34 | -79.991 | 2.8 | 2 | 2118.45 | Greensboro | 14.3 | 41.495 | M | 1607 | 710 | 0.529 | 0.44182 | 8.19% | 0.34485 | 4508.0616 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3686; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3258; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3455; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 4061; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3357; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 3363; Median age 6: 6 |  | 12 | 0.81765 | 0.72271 | 0.7664 | 0.90083 | 0.74467 | 0.746 | [17 empty] | 12 | 27048.3696 | 21180 | 0.78304 | 82 | Tracker | -0.5746% | -20.3429 | 3601.2 | TX | 1 | 0.68217 | -3.138% | [13 empty] | 1.4 | 1 |  |  |  |  | totals&avgs | 25 | 168.6 | 0.87033 | -3.014% |  |  | 11055.0204 | 91514.8931 | 7254.1722 | 292866.5151 | 20302.1788 | 13489.1633 |  |  | 7.641% | 3.4% | 44.5%
13 | 62131 | Red Toad 4451 Buffalo Road, LLC | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 20 | NC | 35.556 | -78.2995 | 3 | 2 | 1789.725 | Raleigh | 15.2 | 39.9515 | C | 1607 | 712 | 0.528 | 0.44306 | 5.435% | 0.49335 | 4295.34 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 4168; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3987; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 4073; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 4037; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 4037; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 4093; Median age 6: 6 |  | 13 | 0.97035 | 0.92822 | 0.94824 | 0.93986 | 0.93986 | 0.95289 | [17 empty] | 13 | 25772.04 | 24395 | 0.94657 | 34 | Fixed | -0.1832% | -7.4571 | 4091.9333 | DE | 0 | [15 empty] | 1.5 | 1 |  |  |  |  | medians |  |  | 0.88714 | -0.4658% |  |  | 6976.2268 | 8103.4289 | 11.8205 | 630.2491 | 311.4385 | 2098.5125 |  |  | 1.352% | 3.1% | 229.3% |  |  | 0.94657 | -0.1832%
14 | 62242 | County of San Diego SBRC | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 10 | CA | 32.632 | -117.077 | 1.4 | 1.3 | 1972.35 | San Diego | 17.9 | 44.009 | M | 1826 | 651.5 | 0.58 | 0.35679 | 0% | 1 | 2209.032 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2344; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2372; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2356; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2394; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2283; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2310; Median age 6: 6 |  | 14 | 1.0611 | 1.0738 | 1.0665 | 1.0837 | 1.0335 | 1.0457 | [17 empty] | 14 | 13254.192 | 14059 | 1.0607 | 2 | Fixed | -0.4853% | -11.4 | 2383.0667 | IL | 0 | [15 empty] | 1.0769 | 1 | [11 empty] | 765.4444 | 137.6711 | 50.8844 | 3196.0178 | 1854.7378 | 21.7778 |  |  | 1.353% | 2.1% | 155.3%
15 | 62039 | Santa Rosa Junior College Petaluma Solar | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 10 | CA | 38.2687 | -122.6336 | 1.3 | 1.2 | 1826.25 | San Francisco | 13.9 | 38.923 | C | 1717 | 629 | 0.575 | 0.36634 | 0% | 1 | 1899.3 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2912; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1947; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 181; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 10; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1826; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 0; Median age 6: 6 |  | 15 | 1.15 | 1.0251 | 0.095298 | 0.0052651 | 0.96141 | 0 | [17 empty] | 15 | 11395.8 | 6876 | 0.60338 | 94 | Fixed | -31.67% | -431.2571 | 2655.4 | MD | 1 | 0.88714 | -2.978% | [13 empty] | 1.0833 | 1 | [11 empty] | 473147.449 | 23751.2131 | 1393883.8237 | 847083.5665 | 1760625.6988 | 4604.5918 |  |  | 75.6% | 2.6% | 3.439% |  |  | 0.60338 | -31.67%
16 | 60851 | Curtis Hill Solar CSG | 2018 | 2016 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | MA | 42.175 | -71.986 | 2.9 | 2 | 1643.625 | Worcester | 8.2 | 31.8655 | C | 1424 | 669 | 0.506 | 0.4698 | 3.318% | 0.64965 | 3813.21 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3214; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3437; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3413; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3338; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3649; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 3237; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 2822; Median age 6: 7 |  | 16 | 0.84286 | 0.90134 | 0.89505 | 0.87538 | 0.95694 | 0.84889 | 0.74006 | [16 empty] | 16 | 26692.47 | 23110 | 0.86579 | 62 | Fixed | -1.439% | -47.8571 | 3492.8571 | OH | 0 | [15 empty] | 1.45 | 2 | [11 empty] | 53361 | 1588.5918 | 4059.5102 | 1337.4694 | 156363.7551 | 978.7959 | 112800.0204 |  | 6.582% | 3.2% | 48.62% |  |  | 0.86579 | -1.439%
17 | 62092 | Montague Site 36-Grosolar | 2019 | 2018 | Electric Utility | c-Si | Other utility | Fixed | 35 | MA | 42.582 | -72.52 | 5 | 4.1 | 1643.625 | Worcester | 8.2 | 31.8655 | C | 1424 | 669 | 0.506 | 0.4698 | 0% | 1 | 6574.5 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 5800; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 5868; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 5066; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 6398; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 5235; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 5933; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 7: 5681; Median age 6: 7 |  | 17 | 0.8822 | 0.89254 | 0.77055 | 0.97315 | 0.79626 | 0.90243 | 0.8641 | [16 empty] | 17 | 46021.5 | 39981 | 0.86875 | 58 | Fixed | -0.03626% | -2.0714 | 5719.8571 | VT | 0 | [15 empty] | 1.2195 | 1 | [11 empty] | 6759.1888 | 23190.9388 | 419441.2704 | 471184.1837 | 225150.25 | 50882.4694 | 593.2704 |  | 7.241% | 3.2% | 44.19% |  |  | 0.86875 | -0.03626%
18 | 62613 | CBP Solar | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 10 | NY | 41.2653 | -73.9579 | 2.4 | 1.8 | 1552.3125 | New York City | 12.6 | 35.5868 | C | 1461 | 682 | 0.509 | 0.4668 | 0.1031% | 0.98668 | 2980.44 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2150; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2472; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2336; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2512; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2319; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 2224; Median age 6: 6 |  | 18 | 0.72137 | 0.82941 | 0.78378 | 0.84283 | 0.77807 | 0.7462 | [17 empty] | 18 | 17882.64 | 14013 | 0.78361 | 78 | Fixed | 0.1065% | 2.4857 | 2326.8 | WA | 0 | [15 empty] | 1.3333 | 1 | [11 empty] | 32143.3673 | 19664.0522 | 3.0376 | 30715.0661 | 409.1951 | 13856.6531 |  |  | 5.438% | 2.7% | 49.65% |  |  | 0.78361 | 0.1065%
19 | 62146 | Minisink Community Solar 2 LLC | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | NY | 41.3194 | -74.5153 | 2.8 | 2 | 1607.1 | Newark | 12.7 | 36.094 | C | 1424 | 682 | 0.495 | 0.47893 | 2.293% | 0.74228 | 3599.904 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3443; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3561; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3453; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3409; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3234; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1012; Median age 6: 6 |  | 19 | 0.95641 | 0.98919 | 0.95919 | 0.94697 | 0.89836 | 0.28112 | [17 empty] | 19 | 21599.424 | 18112 | 0.83854 | 70 | Fixed | -11.74% | -376.5714 | 4336.6667 | NY | 2 | 0.81108 | -5.818% | [13 empty] | 1.4 | 1 | [11 empty] | 267387.4853 | 507.322 | 60539.4308 | 334800.0023 | 608697.1791 | 1134732.1995 |  |  | 20.98% | 3.1% | 14.78% |  |  | 0.83854 | -11.74%
20 | 61944 | Jessamine Solar | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | SC | 34.2305 | -79.3906 | 2.4 | 1.9 | 2154.975 | Wilmington NC | 17.4 | 44.8665 | M | 1644 | 722 | 0.531 | 0.43917 | 5.68% | 0.47789 | 3930.6744 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3077; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3691; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2939; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3682; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3693; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 3596; Median age 6: 6 |  | 20 | 0.78282 | 0.93902 | 0.74771 | 0.93673 | 0.93953 | 0.91486 | [17 empty] | 20 | 23584.0464 | 20678 | 0.87678 | 54 | Tracker | 2.811% | 95.5429 | 3111.9333 | OR | 1 | 1.0411 | 0.03585% | [13 empty] | 1.2632 | 1 | [11 empty] | 17024.0363 | 150529.2194 | 211197.1443 | 35304.6205 | 10681.7146 | 7954.941 |  |  | 7.792% | 3.2% | 41.07%
21 | 62225 | Hunterdon Health System Solar Project | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 25 | NJ | 40.652 | -74.908 | 2 | 1.5 | 1607.1 | Allentown | 10.7 | 34.094 | C | 1424 | 682 | 0.495 | 0.47893 | 1.228% | 0.8525 | 2571.36 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1772; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 2289; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2324; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1609; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 402; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 632; Median age 6: 6 |  | 21 | 0.68913 | 0.89019 | 0.9038 | 0.62574 | 0.15634 | 0.24578 | [17 empty] | 21 | 15428.16 | 9028 | 0.58516 | 98 | Fixed | -20.57% | -345.0286 | 2712.2667 | CT | 1 | 0.98413 | 0.128% | [13 empty] | 1.3333 | 1 | [11 empty] | 354308.39 | 71177.1582 | 418374.8804 | 76644.6042 | 342369.8725 | 101.9138 |  |  | 30.49% | 2.9% | 9.511% |  |  | 0.58516 | -20.57%
22 | 61874 | Eddy II | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | TX | 31.2911 | -97.261 | 14.2 | 10 | 2374.125 | Waco | 19.3 | 48.3955 | M | 1790 | 693 | 0.563 | 0.38715 | 10.42% | 0.25791 | 25621.557 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 18324; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 20266; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 16150; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 17272; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 16248; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 16610; Median age 6: 6 |  | 22 | 0.71518 | 0.79097 | 0.63033 | 0.67412 | 0.63415 | 0.64828 | [17 empty] | 22 | 153729.342 | 104870 | 0.68217 | 86 | Tracker | -3.138% | -557.2 | 19428.5333 | IN | 1 | 0.9363 | -1.234% | [13 empty] | 1.42 | 1 | [11 empty] | 299573.7778 | 3809783.4844 | 2582234.7378 | 5222.4711 | 155656.5511 | 275275.1111 |  |  | 6.236% | 3% | 48.11%
23 | 62224 | Oak Leaf Solar XXVII LLC | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Tracker | 0 | CO | 40.4407 | -104.6455 | 2 | 1.5 | 2337.6 | Boulder | 10.2 | 39.024 | C | 1680 | 603 | 0.579 | 0.35893 | 6.968% | 0.40419 | 3553.152 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 3460; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3539; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 3516; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 3133; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 3413; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 3462; Median age 6: 6 |  | 23 | 0.97378 | 0.99602 | 0.98954 | 0.88175 | 0.96056 | 0.97435 | [17 empty] | 23 | 21318.912 | 20523 | 0.96267 | 26 | Tracker | -0.6253% | -21.4571 | 3495.6 | MN | 5 | 0.91019 | 0.6949% | [13 empty] | 1.3333 | 1 | [11 empty] | 200.0204 | 7450.1559 | 7186.1951 | 76602.4237 | 609.3845 | 9052.1633 |  |  | 3.795% | 5.1% | 134.4% |  |  | 0.96267 | -0.6253%
24 | 62024 | Jefferson Solar (CT) | 2019 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | CT | 41.656 | -72.162 | 1.2 | 1 | 1607.1 | Hartford | 9.9 | 33.294 | C | 1388 | 669 | 0.491 | 0.48199 | 0% | 1 | 1542.816 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 1537; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 1502; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 1446; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 1598; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 1514; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 6: 1513; Median age 6: 6 |  | 24 | 0.99623 | 0.97354 | 0.93725 | 1.0358 | 0.98132 | 0.98067 | [17 empty] | 24 | 9256.896 | 9110 | 0.98413 | 18 | Fixed | 0.128% | 1.9429 | 1511.5333 | RI | 1 | 0.95546 | -0.2119% | [13 empty] | 1.2 | 1 | [11 empty] | 553.3696 | 180.0708 | 5092.5215 | 6192.9405 | 52.528 | 103.8458 |  |  | 2.967% | 2.8% | 94.38% |  |  | 0.98413 | 0.128%
25 | 62074 | Bd of Educ of Queen Anne's Cnty, Cnty HS | 2020 | 2018 | IPP Non-CHP | c-Si | Unknown | Fixed | 30 | MD | 39.0317 | -76.0164 | 2.4 | 2 | 1680.15 | Baltimore | 12.8 | 36.737 | C | 1461 | 696 | 0.498 | 0.47639 | 0% | 1 | 3225.888 | Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 1: 2884; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 2: 3152; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 3: 2836; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 4: 2819; Reported raw MWh per year - a small percentage, roughly 1%, of these numbers are impossibly high and will be capped at no greater than a 1.15 PI on the derived table to the right 5: 2618; Median age 6: 5 |  | 25 | 0.89402 | 0.9771 | 0.87914 | 0.87387 | 0.81156 | [18 empty] | 25 | 16129.44 | 14309 | 0.88714 | 50 | Fixed | -2.978% | -86.5 | 3121.3 | SC | 1 | 0.87678 | 2.811% | [13 empty] | 1.2 | 2 | [11 empty] | 22740.64 | 41493.69 | 665.64 | 1909.69 | 5012.64 |  |  |  | 4.188% | 3% | 71.63% |  |  | 0.88714 | -2.978%
[27 empty] | 2.8765 21: y=mx+b equation to get p90obs/p50 by yr >>; 2.8765 22: #VALUE!; Median age 6: avg>> | #NUM! | p90stat/median | 0.81352 | 0.83831 | 0.62464 | 0.62292 | 0.65331 | 0.4924 | 0.53158 | 0 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | [16 empty] | Total | 25 | 0.87033 | -3.014% | <avg degr
[7 empty] | Developers known to me, but I was too lazy to add them to the named list, include: | [19 empty] | 2.8765 21: y=mx+b equation to get p90stat/p50 by yr >>; 2.8765 22: #VALUE!; Median age 6: avg>> | #N/A | p90obs/median | 0.78096 | 0.8037 | 0.67253 | 0.69462 | 0.67497 | 0.30938 | 0.35758 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [16 empty] | Count (all) | 25 |  | -0.4658% | <median degr
[7 empty] | Cypress Creek Renewables, Altus | [44 empty] | Median | 0.92369 | 0.92822 | 0.93725 | 0.90083 | 0.93953 | 0.90864 | 0.89783 | 0.92051 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | [12 empty] | median> | -0.4658% |  |  | Count (newer 25) | 17 | bar: 2.8765 22 to 2.8765 23
[7 empty] | More significant was the disappearance of the name brand developers that dominated the earlier years | [19 empty] | 2.8765 22: For ex., enter yr# |  | Sys count | 25 | 25 | 25 | 25 | 25 | 22 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1839307.8595 | 1624279 | 0.88309 |  | average> | -3.014%
[27 empty] | 2.8765 22: 8 |  | Rank,p90 | 23 | 23 | 23 | 23 | 23 | 20 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | avg PI > | 0.87033 |  |  | simple average degr rate if all systems are assumed to degrade linearly from year 1.
[27 empty] | 2.8765 22: The p90observed/p50 ratio is: |  | Line#, p90 | 18 | 11 | 22 | 21 | 22 | 19 | 6 | 11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [9 empty] | stdev PI > | 0.13007
[27 empty] | 2.8765 22: #VALUE! |  | p90 (obs.rank) | 0.72137 | 0.74601 | 0.63033 | 0.62574 | 0.63415 | 0.28112 | 0.32105 | 0.92051 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [8 empty] | trkr only | trkr only | PI
[27 empty] | 2.8765 22: The p90statistical/p50 ratio is: |  | Line # | Annual Rankings, seek to find the 90% percentile (i.e., boundary of worst 10%) | [23 empty] | 1417075.9375 | 1264497 | 0.89233 |  |  | -31.67% | this was the worst case degradation (Santa Rosa JC carport)
[27 empty] | 2.8765 22: #VALUE! |  | 1 | 10 | 1 | 1 | 11 | 4 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | fixed only | fixed only
[52 empty] | 2 | 17 | 11 | 7 | 14 | 20 | 15 | 2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | 422231.922 | 359782 | 0.8521
[52 empty] | 3 | 7 | 14 | 12 | 7 | 14 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 4 | 13 | 5 | 8 | 8 | 11 | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 5 | 14 | 16 | 10 | 3 | 2 | 3 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 6 | 2 | 25 | 24 | 24 | 24 | 5 | 6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 7 | 22 | 19 | 22 | 21 | 16 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 8 | 12 | 21 | 4 | 19 | 3 | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 9 | 6 | 3 | 5 | 4 | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 10 | 4 | 7 | 3 | 5 | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 11 | 20 | 23 | 15 | 20 | 22 | 10 | 3 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 12 | 19 | 24 | 20 | 13 | 21 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 13 | 9 | 13 | 11 | 10 | 12 | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 14 | 3 | 2 | 2 | 1 | 1 | 2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 15 | 1 | 4 | 25 | 25 | 8 | 22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 16 | 18 | 15 | 16 | 16 | 10 | 14 | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 17 | 16 | 17 | 19 | 6 | 18 | 12 | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 18 | 23 | 20 | 18 | 18 | 19 | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 19 | 11 | 8 | 9 | 9 | 15 | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 20 | 21 | 12 | 21 | 12 | 13 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 21 | 25 | 18 | 14 | 23 | 25 | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 22 | 24 | 22 | 23 | 22 | 23 | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 23 | 8 | 6 | 6 | 15 | 9 | 6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 24 | 5 | 10 | 13 | 2 | 6 | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | 25 | 15 | 9 | 17 | 17 | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[52 empty] | Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
[52 empty] | Rank,p10 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[52 empty] | Line#, p10 | 14 | 9 | 10 | 5 | 8 | 14 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[52 empty] | p10 (obs.rank) | 1.0611 | 1.049 | 1.0511 | 1.0225 | 1.0129 | 1.0457 | 1.0365 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on BR1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rate evaluated at midpoint of interval (4 yrs)
Note on ED7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used Pendleton for IAV

## ConsolidatedResults
This table created from data in the main PlanData tab, saved as frozen values
America's longest-running PV systems, ranked by lifetime Performance Index, after allowing for an acceptable 0.5%/yr degradation
PI rank # | Name | 1st full yr | Mod type | Structure | State | MWP | TMY2 (Meteonorm at 3 CA sites) | Data yrs | PI (@0.5% degr) | Degradation
1 | Long Island Solar Farm LLC | 2012 | c-Si | Fixed | NY | 37.7 | Bridgeport | 14 | 1.055 | -1.09%
2 | AFA Solar Farm | 2012 | c-Si | Tracker | CO | 6 | Colorado Springs | 13 | 1.0498 | -0.4761%
3 | Greater Sandhill | 2011 | c-Si | Tracker | CO | 20 | Alamosa | 13 | 1.0312 | -0.7406%
4 | Yardville | 2011 | c-Si | Fixed | NJ | 4.3 | Philadelphia | 14 | 1.0243 | -0.1311%
5 | Knouse | 2011 | c-Si | Fixed | PA | 3.2 | Harrisburg | 14 | 1.0237 | -0.5379%
6 | Dover Sun Park | 2012 | c-Si | Tracker | DE | 11.3 | Wilmington DE | 14 | 1.0212 | -2.219%
7 | Kapaa | 2011 | c-Si | Fixed | HI | 1.2 | Lihue | 14 | 1.0104 | -1.364%
8 | Calpine Vineland Solar LLC | 2010 | c-Si | Fixed | NJ | 4.3 | Atlantic City | 15 | 1.0101 | -1.466%
9 | Exelon Chicago | 2010 | Si_IBT | Tracker | IL | 10 | Chicago | 16 | 1.0086 | -1.024%
10 | Atlantic Cty ConvCtr | 2009 | c-Si | Fixed | NJ | 2.4 | Atlantic City | 16 | 1.0076 | -0.5896%
11 | Vineland Mays Landing Solar | 2012 | c-Si | Tracker | NJ | 4.7 | Atlantic City | 13 | 1.0018 | -0.6647%
12 | SPS4 Monument SunE | 2012 | c-Si | Tracker | NM | 10.8 | Midland | 13 | 0.99999 | 0.01945%
13 | Silver Lake | 2011 | c-Si | Fixed | NJ | 2 | Newark | 14 | 0.98333 | -0.1392%
14 | Pocono | 2011 | CdSCdTe | Fixed | PA | 3 | Wilkes-Barre | 14 | 0.97814 | -2.016%
15 | Hyder | 2012 | c-Si | Tracker | AZ | 18.8 | Phoenix | 13 | 0.9757 | -0.4994%
16 | Alamogordo Solar Energy Center | 2012 | CdSCdTe | Fixed | NM | 6.4 | El Paso | 13 | 0.97422 | -0.4579%
17 | DeSoto | 2010 | c-Si | Tracker | FL | 27.6 | Tampa | 15 | 0.96877 | -3.23%
18 | SunE Oxnard | 2010 | CdSCdTe | Fixed | CA | 1.2 | Los Angeles | 15 | 0.96843 | 0.1861%
19 | SMUD at Fleshman | 2012 | CdSCdTe | Fixed | CA | 3.7 | Sacramento | 13 | 0.96645 | -1.893%
20 | 145 Talmadge | 2012 | c-Si | Fixed | NJ | 4.3 | Newark | 13 | 0.96149 | -0.1981%
21 | Shelby | 2011 | Si_IBT | Tracker | NC | 1.035 | Charlotte | 14 | 0.96108 | -2.979%
22 | PG&E Vaca-Dixon | 2010 | c-Si | Fixed | CA | 2.6 | Sacramento | 15 | 0.96013 | -2.04%
23 | Cimarron | 2011 | CdSCdTe | Fixed | NM | 37.4 | Alamosa | 14 | 0.95787 | -1.719%
24 | Space Coast | 2011 | c-Si | Fixed | FL | 11.5 | Daytona Beach | 14 | 0.95514 | -3.359%
25 | Chittenden County Solar Partners | 2012 | c-Si | Tracker | VT | 2.2 | Burlington | 13 | 0.94377 | -1.098%
26 | Webberville | 2012 | c-Si | Tracker | TX | 35 | Austin | 13 | 0.9429 | 0.0292%
27 | Linden | 2011 | c-Si | Fixed | NJ | 3.2 | Newark | 14 | 0.93963 | 0.2326%
28 | Robert O Schulz | 2010 | c-Si | Tracker | CA | 1.51 | Sacramento | 15 | 0.93357 | -3.522%
29 | MF Mesa Ln | 2009 | c-Si | Fixed | PA | 3.1 | Philadelphia | 16 | 0.93197 | -1.127%
30 | Trenton | 2012 | c-Si | Fixed | NJ | 1.3 | Philadelphia | 13 | 0.93146 | -0.441%
31 | Solar Blythe (NRG) | 2010 | CdSCdTe | Fixed | CA | 26.4 | Daggett | 15 | 0.92423 | -1.575%
32 | WEA Texas Bayonne | 2011 | c-Si | Fixed | NJ | 1.7 | Newark | 14 | 0.92391 | 0.1612%
33 | Wyandot | 2011 | CdSCdTe | Fixed | OH | 12 | Mansfield | 15 | 0.92341 | -2.33%
34 | Sunset Reservoir | 2011 | c-Si | Fixed | CA | 5 | San Francisco | 14 | 0.91761 | 0.6024%
35 | Copper Mtn 48 (FS) | 2011 | CdSCdTe | Fixed | NV | 60.5 | Las Vegas | 14 | 0.91497 | -1.005%
36 | Aerojet II | 2011 | c-Si | Tracker | CA | 2.4 | Sacramento | 14 | 0.90785 | -1.371%
37 | Aerojet I | 2011 | c-Si | Tracker | CA | 3.6 | Sacramento | 14 | 0.90773 | -1.642%
38 | RV CSU | 2010 | c-Si | Tracker | CO | 2 | Boulder | 15 | 0.90617 | -2.943%
39 | Copper Mtn10 (FS) | 2009 | CdSCdTe | Fixed | NV | 12.4 | Las Vegas | 16 | 0.90379 | -0.7842%
40 | NEDC Solar Site | 2011 | c-Si | Fixed | MA | 1 | Worcester | 14 | 0.90273 | -0.3137%
41 | Jacksonville | 2011 | CdSCdTe | Fixed | FL | 15 | Jacksonville | 14 | 0.89728 | -3.494%
42 | Wild Horse | 2011 | c-Si | Fixed | WA | 0.5 | Yakima | 15 | 0.89715 | -3.185%
43 | Dow Jones | 2011 | c-Si | Fixed | NJ | 4.1 | Newark | 14 | 0.89024 | -4.461%
44 | Nellis Sunpower | 2008 | Si_IBT | Tracker | NV | 14.2 | Las Vegas | 17 | 0.88833 | -2.917%
45 | Haverhill | 2011 | c-Si | Fixed | MA | 1 | Boston | 14 | 0.88783 | -0.532%
46 | Stroud | 2012 | c-Si | Fixed | CA | 24.6 | Fresno | 13 | 0.88359 | -4.937%
47 | PSEG Hackettstown | 2010 | c-Si | Fixed | NJ | 2.2 | Allentown | 15 | 0.88326 | -1.765%
48 | Cotton Center Solar Hybrid | 2012 | c-Si | Tracker | AZ | 21 | Phoenix | 13 | 0.88219 | -1.196%
49 | CSU Fresno MMA | 2008 | c-Si | Fixed | CA | 1.173 | Fresno | 17 | 0.88031 | -1.663%
50 | Albuquerque Solar Energy Center | 2011 | CdSCdTe | Fixed | NM | 2.4 | Albuquerque | 14 | 0.87963 | 2.941%
51 | Blue Wing | 2011 | CdSCdTe | Fixed | TX | 16.7 | San Antonio | 14 | 0.87555 | -2.573%
52 | Five Points Solar Station | 2012 | c-Si | Fixed | CA | 17.6 | Fresno | 13 | 0.87026 | -4.39%
53 | Sacramento Soleil | 2009 | CdSCdTe | Fixed | CA | 1.2364 | Sacramento | 12 | 0.8645 | -1.72%
54 | Westside Solar Station | 2012 | c-Si | Fixed | CA | 18.5 | Fresno | 13 | 0.85772 | -5.673%
55 | Taylorsville | 2011 | c-Si | Tracker | NC | 1.2 | Charlotte | 14 | 0.85017 | -2.827%
56 | 1420 Coil Av #C | 2011 | c-Si | Fixed | CA | 1.3 | Long Beach | 12 | 0.84827 | -5.474%
57 | Deer Island | 2011 | c-Si | Fixed | MA | 0.736 | Boston | 15 | 0.84809 | 0.2276%
58 | CalRenew-1 | 2011 | c-Si | Fixed | CA | 6.3 | Fresno | 14 | 0.84619 | -5.468%
59 | Perdue Salisbury Photovoltaic | 2012 | c-Si | Fixed | MD | 1.2 | Baltimore | 13 | 0.83875 | -4.149%
60 | SunE Anheuser | 2009 | c-Si | Tracker | CA | 1.2 | Sacramento | 16 | 0.83565 | -4.148%
61 | Hall's Warehouse | 2009 | CdSCdTe | Fixed | NJ | 1.8 | Newark | 16 | 0.81852 | -1.951%
62 | RV CSU Power II | 2011 | c-Si | Fixed | CO | 3.3 | Boulder | 14 | 0.81844 | -3.659%
63 | Western 102 | 2010 | c-Si | Fixed | NV | 1.575 | Reno | 16 | 0.81751 | -2.331%
64 | Mariani Packing SunE | 2009 | c-Si | Tracker | CA | 1.1 | Sacramento | 16 | 0.81169 | -3.556%
65 | Chuckawalla SunE | 2009 | c-Si | Fixed | CA | 1.2 | Daggett | 16 | 0.8097 | -3.995%
66 | Carson | 2010 | c-Si | Fixed | CO | 2 | Colorado Springs | 15 | 0.80672 | -0.3831%
67 | Solar Park Gainesville, LLC | 2012 | c-Si | Fixed | FL | 2 | Jacksonville | 13 | 0.80294 | -5.13%
68 | Vineland West | 2012 | c-Si | Fixed | NJ | 4.8 | Atlantic City | 13 | 0.79765 | -6.862%
69 | SunE Alamosa1 | 2008 | c-Si | Tracker | CO | 9.2 | Alamosa | 17 | 0.79137 | -1.801%
70 | SunE Apple Valley | 2010 | c-Si | Tracker | CA | 1.2 | Daggett | 15 | 0.78337 | -4.679%
71 | Duke Egy 10240 | 2012 | c-Si | Fixed | NC | 2.2 | Charlotte | 13 | 0.77785 | -4.803%
72 | Pennsauken | 2008 | c-Si | Fixed | NJ | 2.4 | Philadelphia | 16 | 0.77673 | -2.171%
73 | SunE LV Sutton | 2009 | c-Si | Tracker | NC | 1.2 | Wilmington NC | 16 | 0.77605 | -4.28%
74 | Kohl's San Bernardino SunE | 2009 | c-Si | Fixed | CA | 1.2 | San Bernardino (Meteonorm) | 16 | 0.77427 | -5.584%
75 | Duke Egy 657 | 2013 | c-Si | Fixed | NC | 1.5 | Greensboro | 12 | 0.76617 | -8.7%
76 | SunE Ironwood | 2009 | c-Si | Tracker | CA | 1.2 | Daggett | 16 | 0.75911 | -5.517%
77 | SunE Moreno Valley | 2009 | c-Si | Fixed | CA | 1.2 | Moreno Valley (Meteonorm) | 16 | 0.75384 | -4.643%
78 | Duke Egy 1725 | 2010 | c-Si | Fixed | NC | 1.2 | Charlotte | 15 | 0.74972 | -1.165%
79 | Haleon York RDC Solar Facility | 2011 | c-Si | Fixed | PA | 3 | Harrisburg | 14 | 0.74538 | -7.192%
80 | LA Harbor College | 2012 | c-Si | Fixed | CA | 2.5 | Long Beach | 13 | 0.74042 | -2.574%
81 | Yamhill Solar LLC | 2012 | c-Si | Fixed | OR | 1.2 | Salem | 13 | 0.73785 | -4.012%
82 | Yolo County | 2011 | Si_IBT | Tracker | CA | 1.1 | Sacramento | 14 | 0.73609 | -9.579%
83 | Woodland Walgreens SunE | 2009 | c-Si | Fixed | CA | 1.2 | Sacramento | 16 | 0.7353 | -4.605%
84 | Crayola | 2013 | c-Si | Fixed | PA | 3.1 | Allentown | 13 | 0.72624 | -1.832%
85 | Meridian Vineyards | 2011 | c-Si | Fixed | CA | 1.3 | Santa Maria | 14 | 0.72192 | -2.177%
86 | Aqua Ingrams Mill | 2010 | c-Si | Fixed | PA | 1.2 | Philadelphia | 14 | 0.72008 | -0.5066%
87 | Denver airport MMA | 2009 | c-Si | Tracker | CO | 2 | Boulder | 16 | 0.70202 | -5.945%
88 | SAS Solar Farm | 2009 | c-Si | Tracker | NC | 2.4 | Raleigh | 16 | 0.695 | -3.313%
89 | Metro Support Services | 2011 | c-Si | Fixed | CA | 1.2 | Los Angeles | 14 | 0.66386 | -8.188%
90 | Roger Rd. WWTP SunE | 2011 | c-Si | Tracker | AZ | 1.1 | Tucson | 14 | 0.65411 | -7.112%
91 | Arizona Western College PV | 2012 | c-Si | Tracker | AZ | 5.6 | Phoenix | 13 | 0.65173 | -5.614%
92 | PPL Merck | 2010 | c-Si | Fixed | NJ | 1.8 | Newark | 15 | 0.64217 | -4.912%
93 | Bayville Central | 2010 | c-Si | Fixed | NJ | 0.28 | Atlantic City | 15 | 0.62907 | -2.689%
94 | UASTP I | 2012 | c-Si | Tracker | AZ | 1.6 | Tucson | 13 | 0.60182 | -8.332%
95 | MMA Bolthouse | 2009 | c-Si | Tracker | CA | 1.9055 | Daggett | 16 | 0.59743 | -7.905%
96 | WWRF Rifle SunE | 2010 | c-Si | Tracker | CO | 2.2 | Grand Junction | 15 | 0.58584 | -3.755%
97 | Lanai Sunpower | 2009 | Si_IBT | Tracker | HI | 1.4784 | Kahului | 16 | 0.44454 | -9.915%
98 | Solar PV #02 (SCE) | 2010 | CdSCdTe | Fixed | CA | 1.2 | Chino (Meteonorm) | 15 | 0.42784 | -8.512%
99 | Agua Fria PV-3 | 2003 | c-Si | Tracker | AZ | 0.2576 | Phoenix | 23 | 0.39997 | -7.688%
100 | Pacific Cruise | 2011 | c-Si | Fixed | CA | 1.079 | Long Beach | 14 | 0.34363 | -20.74%

## References
https://www.sustainablebusiness.com/2008/10/wm-bolthouse-farms-gets-19-mw-solar-array-43804/
10300 | qty Mitsubishi, assume 185 W |  |  | 1905.5 | kWp
https://www.mwra.com/our-environment/sustainability/renewable-energy
736 | kW | as of | 2011
https://www.renewableenergyworld.com/solar/castle-cooke-to-build-1-5-mw-solar-farm-on-lanai-hawaii-48828/
https://vfinal.ai/resources/plants/56875/
this is for the Sacramento Soleil EDF First Solar weirdo system in Wilton
https://www.gridinfo.com/plant/western-102-power-plant/56500
Western 102. Reported dc capacity looks way low. Counting modules of that size (1.6 m x 1 m) and vintage, Sharp, a leader at the time, had a 200 W model. 200 W x 7875= 1.57 MWp
For Kohl's San Bernardino, 57009, use Meteonorm at 10 degree POA
56889 NJ Merck: azimuth is SE but slope appears to be negligible, so use Newark GHI
https://vfinal.ai/resources/plants/57204/
PSEG Hackettstown - gridonfo didn't reveal specs such as tilt angle or dc or ac size
https://newsroom.edison.com/releases/southern-california-edison-connects-32-acre-5-million-watt-solar-array-to-its-grid
Media Contact: Gil Alexander, (626) 302-2255
Can't find info on 56996, Solar Photovoltaic Project #02. Called SCE on 4/21 to ask for location and metadata; the "helpful" media rep Diane Castro says nope, won't tell you shit because of "privacy." Right. The fucking thing hasn't operated since 2022, so it ran for 13 of its design 30 years. Weeeee!
https://www.californiadgstats.ca.gov/downloads/
Sleuthing it out, maybe this is a two Satcon x 500 kW ac, and 808 kWp array in Fontana. Filtering the CSI Working Data set for SCE systems in 2009, this is the only one large enough to meet the possibility. Mitsubishi mods, Fixed 30 south.
https://www.powermag.com/california-greenlights-sces-solar-rooftop-program/
This ref suggest it's a First Solar job for SCE's #1 and #2 installs, with the second on a Chino rooftop of 458,000 sq ft industrial
https://www.acua.com/ACUA/media/Acua/uploadedfiles/Solar-Array-Project-Fact-Sheet-2025.pdf#:~:text=The%20Solar%20Electric%20or%20Photovoltaic%20(PV)%20project,with%202%2C700%20electric%20modules%20or%20panels%20installed.
For 54569, NJ Bayville, assume this reporting covers 280 kW of the 500 kW 2-phase project
https://www.joc.com/article/port-of-los-angeles-completes-one-megawatt-solar-project-on-rooftop-of-world-cruise-center-5649339
This is for location and size and specs for Pacific Cruise Ship Terminals Berth 93
https://whosonthemove.com/duke-energy-commercial-solar-power-project-producing-electricity-in-shelby-n-c-163433/
Sunpower Duke NC, assume 230 W modules of that vintage, link says qty 4,500
Above size ref for shitty EIA #57310
For Robert Schulz tracker 2008-09, started for real 2010, a May 2026 EPRI repowering report gave the true shit for this one: 417.6 kW Foirst Solar, 5760 mods by my count, so 72,5 W each, plus 6720 Conergy 175 W, and 7 x 250 kW Xantrex (misspelled Xantrax) inverters
file:///C:/Users/50pea/Downloads/3002034859_PV%20Plant%20Decommissioning%20and%20Repowering%20Case%20Study_%20Robert%20O.%20Schulz%20Solar%20Farm,%20South%20San%20Joaquin%20Irrigation%20District.PDF

## Recipe
Step
1 | Go to EIA.gov and sort to get Solar only, for all states
2 | Restrict display to an early year. I started at 2005, then let in 2006 newcomers, 2007 etc.
3 | Click on an alphabetically listed candidate. When its performance page loads, scroll up to its annual MWh graph to see if it makes sense in terms of duration and eyeball when it looks to be into its full operation period
4 | Click download on its table CSV data, and paste that series of horizontally aligned annual outputs directly into this worksheet on the PlantData tab
5 | Check the gridinfo.com website and fish around to find the specs for the system using a state search and if necessary, search the general internet to get the system's lat/long and size data
6 | Look at the site in Google Earth once you've found its lat/long. Take a look at historical imagery to see if the system has been altered or removed. Take note of its orientation - fixed or tracker, azimuth, tilt…
7 | Look up the nearest TMY2 annual average POA for the nearest orientation
8 | Add the new series to the graph in the PI tab, and fiddle with its line and marker to look as unique as possible

## States100
| States | # systems |  | Sectors | # systems |  | TMY2 Source | # systems | Lat | Long |  | Tmod ranking | TMY2 Source | Tmod | Range
1 | CA | 30 | 1 | Commercial CHP | 2 | 1 | Sacramento | 10 | 38.52 | -121.5 |  | 1 | Kahului | 56.0105 | H
2 | NJ | 16 | 2 | Commercial Non-CHP | 9 | 2 | Newark | 7 | 40.7 | -74.17 |  | 2 | Phoenix | 55.768 | H
3 | CO | 8 | 3 | Electric Utility | 24 | 3 | Atlantic City | 5 | 39.45 | -74.57 |  | 3 | Phoenix | 55.768 | H
4 | NC | 7 | 4 | Industrial Non-CHP | 2 | 4 | Daggett | 5 | 34.87 | -116.78 |  | 4 | Phoenix | 55.768 | H
5 | AZ | 6 | 5 | IPP Non-CHP | 63 | 5 | Fresno | 5 | 36.77 | -119.72 |  | 5 | Phoenix | 55.768 | H
6 | PA | 6 |  |  | 100 | 6 | Philadelphia | 5 | 39.88 | -75.25 |  | 6 | Daggett | 54.4613 | H
7 | FL | 4 |  |  |  | 7 | Charlotte | 4 | 38.52 | -121.5 |  | 7 | Las Vegas | 54.3391 | H
8 | NM | 4 |  |  |  | 8 | Phoenix | 4 | 33.43 | -112.02 |  | 8 | Daggett | 54.054 | H
9 | NV | 4 |  |  |  | 9 | Alamosa | 3 | 37.45 | -105.87 |  | 9 | Daggett | 54.054 | H
10 | MA | 3 |  |  |  | 10 | Boulder | 3 | 40.02 | -105.25 |  | 10 | Tucson | 53.6395 | H
11 | HI | 2 |  |  |  | 11 | Las Vegas | 3 | 36.08 | -115.17 |  | 11 | Tucson | 53.6395 | H
12 | TX | 2 |  |  |  | 12 | Long Beach | 3 | 33.82 | -118.15 |  | 12 | Tampa | 50.9525 | H
13 | DE | 1 |  |  |  | 13 | Allentown | 2 | 40.65 | -75.43 |  | 13 | Lihue | 49.766 | M
14 | IL | 1 |  |  |  | 14 | Boston | 2 | 42.37 | -71.03 |  | 14 | Austin | 49.124 | M
15 | MD | 1 |  |  |  | 15 | Colorado Springs | 2 | 38.82 | -104.72 |  | 15 | Daggett | 48.8955 | M
16 | NY | 1 |  |  |  | 16 | Harrisburg | 2 | 40.22 | -76.85 |  | 16 | Daggett | 48.8955 | M
17 | OH | 1 |  |  |  | 17 | Jacksonville | 2 | 30.5 | -81.7 |  | 17 | Midland | 48.6675 | M
18 | OR | 1 |  |  |  | 18 | Los Angeles | 2 | 33.93 | -118.4 |  | 18 | Las Vegas | 48.324 | M
19 | VT | 1 |  |  |  | 19 | Tucson | 2 | 32.12 | -110.93 |  | 19 | Las Vegas | 48.324 | M
20 | WA | 1 |  |  |  | 20 | Albuquerque | 1 | 35.05 | -106.62 |  | 20 | Daytona Beach | 46.866 | M
|  | 100 |  |  |  | 21 | Austin | 1 | 30.3 | -97.7 |  | 21 | San Antonio | 46.3004 | M
[6 empty] | 22 | Baltimore | 1 | 39.18 | -76.67 |  | 22 | El Paso | 46.124 | M
[6 empty] | 23 | Bridgeport | 1 | 41.17 | -73.13 |  | 23 | Sacramento | 45.91 | M
[6 empty] | 24 | Burlington | 1 | 44.47 | -73.15 |  | 24 | Sacramento | 45.91 | M
[6 empty] | 25 | Chicago | 1 | 41.78 | -87.75 |  | 25 | Sacramento | 45.91 | M
[6 empty] | 26 | Chino (Meteonorm) | 1 | 33.99 | -117.7 |  | 26 | Sacramento | 45.91 | M
[6 empty] | 27 | Daytona Beach | 1 | 29.18 | -81.05 |  | 27 | Sacramento | 45.91 | M
[6 empty] | 28 | El Paso | 1 | 31.8 | -106.4 |  | 28 | Sacramento | 45.91 | M
[6 empty] | 29 | Grand Junction | 1 | 39.12 | -108.53 |  | 29 | San Bernardino (Meteonorm) | 45.585 | M
[6 empty] | 30 | Greensboro | 1 | 36.08 | -79.95 |  | 30 | Moreno Valley (Meteonorm) | 44.7936 | M
[6 empty] | 31 | Kahului | 1 | 20.9 | -156.43 |  | 31 | Jacksonville | 44.7515 | M
[6 empty] | 32 | Lihue | 1 | 21.98 | -159.35 |  | 32 | Jacksonville | 44.7515 | M
[6 empty] | 33 | Mansfield | 1 | 40.82 | -82.52 |  | 33 | Fresno | 44.3235 | M
[6 empty] | 34 | Midland | 1 | 31.93 | -102.2 |  | 34 | Fresno | 44.3235 | M
[6 empty] | 35 | Moreno Valley (Meteonorm) | 1 | 33.8659 | -117.2215 |  | 35 | Fresno | 44.3235 | M
[6 empty] | 36 | Raleigh | 1 | 35.87 | -78.78 |  | 36 | Fresno | 44.3235 | M
[6 empty] | 37 | Reno | 1 | 39.5 | -119.78 |  | 37 | Long Beach | 43.6017 | M
[6 empty] | 38 | Salem | 1 | 44.92 | -123.02 |  | 38 | Los Angeles | 43.5805 | M
[6 empty] | 39 | San Antonio | 1 | 29.53 | -98.47 |  | 39 | Fresno | 43.2484 | M
[6 empty] | 40 | San Bernardino (Meteonorm) | 1 | 34.0947 | -117.2668 |  | 40 | Long Beach | 43.1945 | M
[6 empty] | 41 | San Francisco | 1 | 37.62 | -122.38 |  | 41 | Long Beach | 43.1945 | M
[6 empty] | 42 | Santa Maria | 1 | 34.9 | -120.45 |  | 42 | Chino (Meteonorm) | 43.1303 | M
[6 empty] | 43 | Tampa | 1 | 27.97 | -82.53 |  | 43 | Charlotte | 42.795 | M
[6 empty] | 44 | Wilkes-Barre | 1 | 41.33 | -75.73 |  | 44 | Charlotte | 42.795 | M
[6 empty] | 45 | Wilmington DE | 1 | 39.67 | -75.6 |  | 45 | Sacramento | 42.3805 | M
[6 empty] | 46 | Wilmington NC | 1 | 34.27 | -77.9 |  | 46 | Los Angeles | 42.3588 | M
[6 empty] | 47 | Worcester | 1 | 42.27 | -71.87 |  | 47 | Sacramento | 42.2312 | M
[6 empty] | 48 | Yakima | 1 | 46.57 | -120.53 |  | 48 | Grand Junction | 42.153 | M
[8 empty] | "Avg" Location >> | 36.4219 | -100.2018 | Wichita! | 49 | Raleigh | 42.1235 | M
[8 empty] | Northernmost | 46.57 | Yakima |  | 50 | Sacramento | 42.0819 | M
[8 empty] | Southernmost | 20.9 | Kahului |  | 51 | Albuquerque | 41.9525 | M
[8 empty] | Easternmost | -71.03 | Boston |  | 52 | Santa Maria | 41.4769 | M
[8 empty] | Westernmost | -159.35 | Lihue |  | 53 | Sacramento | 41.2606 | M
[8 empty] | "Avg" Location (excl. HI) >> | 37.0733 | -97.6937 |  | 54 | Wilmington NC | 39.7665 | C
[12 empty] | 55 | Charlotte | 39.6728 | C
[12 empty] | 56 | Alamosa | 39.354 | C
[12 empty] | 57 | Charlotte | 39.3334 | C
[12 empty] | 58 | Boulder | 39.024 | C
[12 empty] | 59 | Boulder | 39.024 | C
[12 empty] | 60 | Colorado Springs | 38.8385 | C
[12 empty] | 61 | Greensboro | 38.6646 | C
[12 empty] | 62 | San Francisco | 38.5157 | C
[12 empty] | 63 | Wilmington DE | 38.1375 | C
[12 empty] | 64 | Alamosa | 37.7781 | C
[12 empty] | 65 | Reno | 37.595 | C
[12 empty] | 66 | Atlantic City | 37.5375 | C
[12 empty] | 67 | Baltimore | 36.737 | C
[12 empty] | 68 | Boulder | 36.309 | C
[12 empty] | 69 | Newark | 36.094 | C
[12 empty] | 70 | Newark | 36.094 | C
[12 empty] | 71 | Philadelphia | 36.0655 | C
[12 empty] | 72 | Philadelphia | 36.0655 | C
[12 empty] | 73 | Philadelphia | 36.0655 | C
[12 empty] | 74 | Philadelphia | 36.0655 | C
[12 empty] | 75 | Atlantic City | 35.637 | C
[12 empty] | 76 | Atlantic City | 35.637 | C
[12 empty] | 77 | Colorado Springs | 35.5805 | C
[12 empty] | 78 | Newark | 35.4153 | C
[12 empty] | 79 | Newark | 35.4153 | C
[12 empty] | 80 | Newark | 35.4153 | C
[12 empty] | 81 | Philadelphia | 35.3867 | C
[12 empty] | 82 | Harrisburg | 35.2655 | C
[12 empty] | 83 | Newark | 35.008 | C
[12 empty] | 84 | Atlantic City | 34.8225 | C
[12 empty] | 85 | Atlantic City | 34.8225 | C
[12 empty] | 86 | Newark | 34.7365 | C
[12 empty] | 87 | Chicago | 34.6945 | C
[12 empty] | 88 | Yakima | 34.38 | C
[12 empty] | 89 | Boston | 34.3655 | C
[12 empty] | 90 | Bridgeport | 34.294 | C
[12 empty] | 91 | Allentown | 34.094 | C
[12 empty] | 92 | Allentown | 34.094 | C
[12 empty] | 93 | Salem | 34.051 | C
[12 empty] | 94 | Harrisburg | 33.9623 | C
[12 empty] | 95 | Burlington | 33.652 | C
[12 empty] | 96 | Boston | 33.551 | C
[12 empty] | 97 | Alamosa | 33.1095 | C
[12 empty] | 98 | Mansfield | 32.551 | C
[12 empty] | 99 | Wilkes-Barre | 32.351 | C
[12 empty] | 100 | Worcester | 30.4906 | C
[13 empty] | Average Tmod | 41.7722
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Meteonorm was used for three SoCal sites, since they’re not like LA, Long Beach, or Daggett
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## States25
| States | # systems |  | Sectors | # systems |  | TMY2 Source | # systems | Lat | Long |  | Tmod ranking | TMY2 Source | Tmod | Range
1 | MN | 5 | 1 | Commercial CHP | 0 | 1 | Minneapolis | 3 | 44.88 | -93.22 |  | 1 | Tampa | 50.9525 | H
2 | CA | 2 | 2 | Commercial Non-CHP | 0 | 2 | Worcester | 2 | 42.27 | -71.87 |  | 2 | Waco | 48.3955 | M
3 | MA | 2 | 3 | Electric Utility | 3 | 3 | Albuquerque | 1 | 35.05 | -106.62 |  | 3 | Tucson | 47.938 | M
4 | NC | 2 | 4 | Industrial Non-CHP | 0 | 4 | Allentown | 1 | 40.65 | -75.43 |  | 4 | Albuquerque | 46.025 | M
5 | NY | 2 | 5 | IPP Non-CHP | 22 | 5 | Baltimore | 1 | 39.18 | -76.67 |  | 5 | Wilmington NC | 44.8665 | M
6 | AZ | 1 |  |  | 25 | 6 | Boulder | 1 | 40.02 | -105.25 |  | 6 | San Diego | 44.009 | M
7 | CO | 1 |  |  |  | 7 | Evansville | 1 | 38.05 | -87.53 |  | 7 | Greensboro | 41.495 | M
8 | CT | 1 |  |  |  | 8 | Greensboro | 1 | 36.08 | -79.95 |  | 8 | Raleigh | 39.9515 | C
9 | FL | 1 |  |  |  | 9 | Hartford | 1 | 41.93 | -72.68 |  | 9 | Boulder | 39.024 | C
10 | IN | 1 |  |  |  | 10 | New York City | 1 | 40.78 | -73.97 |  | 10 | San Francisco | 38.923 | C
11 | MD | 1 |  |  |  | 11 | Newark | 1 | 40.7 | -74.17 |  | 11 | WyEast (Meteonorm) | 37.592 | C
12 | NJ | 1 |  |  |  | 12 | Providence | 1 | 41.73 | -71.43 |  | 12 | Evansville | 37.4085 | C
13 | NM | 1 |  |  |  | 13 | Raleigh | 1 | 35.87 | -78.78 |  | 13 | Baltimore | 36.737 | C
14 | OR | 1 |  |  |  | 14 | Rochester | 1 | 43.92 | -92.5 |  | 14 | Newark | 36.094 | C
15 | RI | 1 |  |  |  | 15 | Saint Cloud | 1 | 45.55 | -94.07 |  | 15 | New York City | 35.5868 | C
16 | SC | 1 |  |  |  | 16 | San Diego | 1 | 32.73 | -117.17 |  | 16 | Allentown | 34.094 | C
17 | TX | 1 |  |  |  | 17 | San Francisco | 1 | 37.62 | -122.38 |  | 17 | Providence | 33.8655 | C
|  | 25 |  |  |  | 18 | Tampa | 1 | 27.97 | -82.53 |  | 18 | Hartford | 33.294 | C
[6 empty] | 19 | Tucson | 1 | 32.12 | -110.93 |  | 19 | Minneapolis | 33.0375 | C
[6 empty] | 20 | Waco | 1 | 31.62 | -97.22 |  | 20 | Worcester | 31.8655 | C
[6 empty] | 21 | Wilmington NC | 1 | 34.27 | -77.9 |  | 21 | Worcester | 31.8655 | C
[6 empty] | 22 | WyEast (Meteonorm) | 1 | 45.5846 | -120.5999 |  | 22 | Minneapolis | 31.137 | C
[8 empty] | "Avg" Location >> | 38.5716 | -90.1305 | St. Louis! | 23 | Minneapolis | 31.137 | C
[8 empty] | Northernmost | 45.5846 | WyEast (Meteonorm) |  | 24 | Rochester | 30.0655 | C
[8 empty] | Southernmost | 27.97 | Tampa |  | 25 | Saint Cloud | 29.237 | C
[8 empty] | Easternmost | -71.43 | Providence
[8 empty] | Westernmost | -122.38 | San Francisco |  |  | Average Tmod | 37.7839
[13 empty] | Bin | #
[13 empty] | >40 | 18 | C
[13 empty] | 40to50 | 6 | M
[13 empty] | >50 | 1 | H
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Meteonorm was used for three SoCal sites, since they’re not like LA, Long Beach, or Daggett

## EIAthru2010
Plants for multiple sectors,multiple states,solar
https://www.eia.gov/beta/electricity/data/browser/#/topic/1?agg=2,0,1&fuel=0000001&pt=&pm=&sec=vvo&geo=vvvvvvvvvvvvo&wd=&ws=&wsn=&wt=&freq=A&datecode=2010&tab=overview&pin=&rse=0&maptype=0&ltype=pin&ctype=linechart&end=201710&start=200101
Fri Apr 03 2026 20:33:58 GMT-0700 (Pacific Daylight Time)
Source: U.S. Energy Information Administration
Plant Name | Plant Code | State | Sector Name | Prime Movers | Fuel Types | Primary Technology
Agua Fria | 141 | AZ | Electric Utility | GT, PV, ST | NG, SUN | Multiple
Aqua Ingrams Mill | 57280 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 106 | systems
Atlantic City Convention Center | 56900 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 76 | qualified to include by Tim
Ausra Kimberlina Solar Generation | 56943 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 71.7%
Bayville Central Facility | 54569 | NJ | Commercial CHP | IC, PV | DFO, OBG, SUN | Multiple
Belmar Solar Array | 56861 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Blue Wing Solar Energy Generation | 57197 | TX | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Bolthouse S&P and Rowen Farms Solar | 56862 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
CM10 | 56944 | NV | IPP Non-CHP | PV | SUN | Solar Photovoltaic
CM48 | 57205 | NV | IPP Non-CHP | PV | SUN | Solar Photovoltaic
CSU Fresno Solar Project | 56813 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
CalRenew-1 | 56768 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Calpine Vineland Solar LLC | 57081 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Carson Solar I | 57509 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Chuckawalla Valley State Prison | 57011 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Cimarron Solar Facility | 57243 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Crayola Solar Project | 57216 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
DE Solar 10240 Old Dowd Rd | 57334 | NC | Electric Utility | PV | SUN | Solar Photovoltaic
DE Solar 1725 Drywall Dr | 57336 | NC | Electric Utility | PV | SUN | Solar Photovoltaic
DE Solar 657 Brigham Rd | 57335 | NC | Electric Utility | PV | SUN | Solar Photovoltaic
DOE Golden NREL Main Campus | 57694 | CO | Commercial Non-CHP | PV | SUN | Solar Photovoltaic
DOE Golden NWTC Building Side | 57692 | CO | Commercial Non-CHP | PV | SUN | Solar Photovoltaic
DeSoto Next Generation Solar Energy | 56929 | FL | Electric Utility | PV | SUN | Solar Photovoltaic
Deer Island Treatment Plant | 10823 | MA | Commercial CHP | GT, HY, PV, ST, WT | DFO, OBG, SUN, WAT, WND | Multiple
Denver Int Airport | 56815 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Dow Jones South Brunswick Solar | 57397 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
ELACC Photovoltaic Power Facility | 56814 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
ETS Ewing Solar Facility | 57574 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Exelon Solar Chicago | 57191 | IL | IPP Non-CHP | PV | SUN | Solar Photovoltaic
FRV SI Transport Solar LP | 57506 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Gap Pacific Distribution Center | 56909 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Greater Sandhill I | 57377 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Haleon York RDC Solar Facility | 57390 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Hall's Warehouse Solar Project | 56877 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Haverhill Solar Power Project | 57269 | MA | Electric Utility | PV | SUN | Solar Photovoltaic
Jacksonville Solar | 57202 | FL | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Kapaa Photovoltaic Project | 57525 | HI | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Knouse Solar Project 1 | 57412 | PA | Industrial Non-CHP | PV | SUN | Solar Photovoltaic
Kohls San Bernardino Solar Facility | 57009 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Lanai Solar-Electric Plant | 56667 | HI | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Linden Solar Farm | 57381 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic
Lockhart Solar PV, LLC | 10444 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
Los Angeles Harbor College | 57314 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
MF Mesa Lane LLC | 56993 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
MMA RC Power LP | 56574 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Mariani Packing Vacaville Solar | 57005 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Maricopa Solar | 57140 | AZ | IPP Non-CHP | OT | SUN | Solar Thermal without Energy Storage
Metro Support Services Center Solar | 57313 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
NEDC Solar Site | 57270 | MA | Electric Utility | PV | SUN | Solar Photovoltaic
Nellis Air Force Base Solar Array | 56568 | NV | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Nevada Solar One | 56405 | NV | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
Ocotillo | 116 | AZ | Electric Utility | GT, PV, ST | NG, SUN | Multiple
PPL Renewable Energy Merck Solar | 56889 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
PSEG Hackettstown | 57204 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Pacific Cruise Ship Terminals Berth 93 | 57309 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Pennsauken Solar | 56883 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Pocono Solar Project | 57367 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Prescott Airport | 56228 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic
RMQ 1 and 2 | 56966 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic
RV CSU Power II LLC | 57507 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
RV CSU Power LLC | 57141 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Rancho Seco Solar | 529 | CA | Electric Utility | PV | SUN | Solar Photovoltaic
Robert O Schulz Solar Farm | 57579 | CA | Electric Utility | PV | SUN | Solar Photovoltaic
Roger Road WWTP | 57524 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SAS Solar Farm | 56915 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SEGS III | 10439 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
SEGS IV | 10440 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
SEGS IX | 10446 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
SEGS V | 10441 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
SEGS VI | 10442 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
SEGS VII | 10443 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
Sacramento Soleil LLC | 56875 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Saguaro | 118 | AZ | Electric Utility | GT, OT, ST | NG, SUN | Multiple
Shelby Solar Energy Generation Facility | 57200 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Sierra SunTower Solar Gen Station | 57323 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
Silver Lake Solar Farm | 57341 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic
Solar Blythe LLC | 56939 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Solar Photovoltaic Project #01 | 56976 | CA | Electric Utility | PV | SUN | Solar Photovoltaic
Solar Photovoltaic Project #02 | 56996 | CA | Electric Utility | PV | SUN | Solar Photovoltaic
Space Coast Next Gen Solar Energy | 56930 | FL | Electric Utility | PV | SUN | Solar Photovoltaic
Springerville | 8223 | AZ | Electric Utility | PV, ST | SUB, SUN | Multiple
State-Fuel Level Increment | 99999 | -- | -- | -- | -- | --
Sun Farmer I | 57445 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunE Alamosa | 56481 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunEdison Anheuser Busch Fairfield | 57010 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunEdison Ironwood State Prison | 57007 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunEdison LV Sutton Plant Site | 56938 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunEdison Procter & Gamble Oxnard | 57008 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunEdison Walgreens Moreno Valley | 57004 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
SunEdison Walmart Apple Valley DC | 57012 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Sunray 2 | 10437 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
Sunray 3 | 10438 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage
Sunset Reservoir North Basin | 57559 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Taylorsville Solar LLC | 57402 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Trenton Solar Farm | 57352 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic
UASTP I | 57392 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic
Vaca Dixon Solar Station | 57041 | CA | Electric Utility | PV | SUN | Solar Photovoltaic
Victor Valley CC CPV Solar | 57254 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic
WEA Texas Bayonne | 57383 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic
WWRF Solar Plant | 56922 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Walgreens Woodland Distribution Center | 57006 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Western 102 Power Plant | 56500 | NV | Industrial Non-CHP | IC, PV | NG, SUN | Multiple
Wild Horse | 56322 | WA | Electric Utility | PV, WT | SUN, WND | Multiple
Wyandot Solar Farm | 57203 | OH | IPP Non-CHP | PV | SUN | Solar Photovoltaic
Yardville Solar Farm | 57382 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic
Yolo County Solar Project | 57422 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic

## EIAthru2011
| Plants for multiple sectors,multiple states,solar | [10 empty] | 229 | systems
| https://www.eia.gov/beta/electricity/data/browser/#/topic/1?agg=2,0,1&fuel=0000001&pt=&pm=&sec=vvo&geo=vvvvvvvvvvvvo&wd=&ws=&wsn=&wt=&freq=A&datecode=2011&tab=overview&start=200101&end=201710&ctype=linechart&ltype=pin&maptype=0&rse=0&pin= | [10 empty] | 123 | new ones added in 2011
| Fri Apr 03 2026 20:35:53 GMT-0700 (Pacific Daylight Time) | [10 empty] | 106 | listed through 2010
in 2011, | Source: U.S. Energy Information Administration | [6 empty] | 104
EIA list# | Plant Name | Plant Code | State | Sector Name | Prime Movers | Fuel Types | Primary Technology | Match w/previous | New? | Running total | Include in last batch of 24 for the Top 100?
1 | 1420 Coil Av #C | 57310 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 77 | Y
2 | 145 Talmadge Solar | 57458 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 78 | Y
3 | 500 Virginia Solar | 57640 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 79 | Y
4 | AFA Solar Farm | 57554 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 80 | Y
5 | Aerojet I | 57697 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 81 | Y
6 | Aerojet II | 57698 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 82 | Y
7 | Agua Fria | 141 | AZ | Electric Utility | GT, PV, ST | NG, SUN | Multiple | 1 | No | 82 | N
8 | Alamogordo Solar Energy Center | 57577 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 83 | Y
9 | Albuquerque Solar Energy Center | 57567 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 84 | Y
10 | Aqua Ingrams Mill | 57280 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 84 | N
11 | Arizona Western College PV | 57765 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 | Y
12 | Atlantic City Convention Center | 56900 | NJ | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
13 | Ausra Kimberlina Solar Generation | 56943 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 85 | N
14 | Avenal Park | 57359 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | CA
15 | Bakersfield College Solar 01 | 57655 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | CA
16 | Bayville Central Facility | 54569 | NJ | Commercial CHP | IC, PV | DFO, OBG, SUN | Multiple | 1 | No | 85 | N
17 | Bellevue Solar Project | 57372 | OR | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 | N
18 | Belmar Solar Array | 56861 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
19 | Benjamin Moore & Co. Solar | 57733 | NJ | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | NJ
20 | Blue Wing Solar Energy Generation | 57197 | TX | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
21 | Bolthouse S&P and Rowen Farms Solar | 56862 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
22 | CASD Solar | 57668 | PA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | PA
23 | CM10 | 56944 | NV | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
24 | CM48 | 57205 | NV | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
25 | CS Murphy Point, LLC | 57687 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | NC
26 | CSU Fresno Solar Project | 56813 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
27 | CalRenew-1 | 56768 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
28 | Calpine Vineland Solar LLC | 57081 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
29 | Carson Solar I | 57509 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 85 | N
30 | Castle Rock Vineyards | 57870 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | CA
31 | Cherry Hill | 57734 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 85 |  | NJ
32 | Chittenden County Solar Partners | 57481 | VT | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 86 | Y
33 | Chuckawalla Valley State Prison | 57011 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 86 | N
34 | Cimarron Solar Facility | 57243 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 86 | N
35 | City & County of Denver at Denver Int'l | 57645 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 86 |  | CO
36 | City of Boulder WWTP | 57681 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 86 |  | CO
37 | City of Madera WWTP | 57682 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 86 |  | CA
38 | Cotton Center Solar Hybrid | 57561 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 87 | Y
39 | Crayola Solar Project | 57216 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
40 | DE Solar 10240 Old Dowd Rd | 57334 | NC | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
41 | DE Solar 1725 Drywall Dr | 57336 | NC | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
42 | DE Solar 657 Brigham Rd | 57335 | NC | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
43 | DOE Golden NREL Main Campus | 57694 | CO | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
44 | DOE Golden NWTC Building Side | 57692 | CO | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
45 | Dartmouth Solar | 57473 | MA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 87 |  | MA
46 | DeSoto Next Generation Solar Energy | 56929 | FL | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
47 | Deer Island Treatment Plant | 10823 | MA | Commercial CHP | GT, HY, PV, ST, WT | DFO, OBG, SUN, WAT, WND | Multiple | 1 | No | 87 | N
48 | Deming Solar Energy Center | 57575 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 87 |  | NM
49 | Denver Int Airport | 56815 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 87 | N
50 | Dinuba Wastewater Treatment Plant | 57827 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 87 |  | CA
51 | Dover Sun Park | 57337 | DE | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 88 | Y
52 | Dow Jones South Brunswick Solar | 57397 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 88 | N
53 | ELACC Photovoltaic Power Facility | 56814 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 88 | N
54 | ETS Ewing Solar Facility | 57574 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 88 | N
55 | Exelon Solar Chicago | 57191 | IL | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 88 | N
56 | FRB Solar Farm | 57930 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 88 |  | AZ
57 | FRV SI Transport Solar LP | 57506 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 88 | N
58 | FedEx Field Solar Facility | 57747 | MD | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 88 | N
59 | FedEx Woodbridge | 57776 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 88 |  | NJ
60 | Five Points Solar Station | 57498 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 89 | Y
61 | Flemington Solar | 57485 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 89 |  | NJ
62 | Frenchtown II Solar | 57487 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 89 |  | NJ
63 | Gap Pacific Distribution Center | 56909 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 89 | N
64 | Greater Sandhill I | 57377 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 89 | N
65 | Haleon York RDC Solar Facility | 57390 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 89 | N
66 | Hall's Warehouse Solar Project | 56877 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 89 | N
67 | Hatch Solar Energy Center I, LLC | 57591 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 89 | N
68 | Haverhill Solar Power Project | 57269 | MA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 89 | N
69 | Heller Industrial Parks | 57869 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 89 |  | NJ
70 | Holyoke Solar Cooperative at Mueller | 57931 | MA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 89 |  | MA
71 | Hyder Solar Hybrid | 57563 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 | Y
72 | ISH Solar Central, LLC | 57799 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
73 | ISH Solar Hospital Downey | 57841 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | CA
74 | ISH Solar Hospital SDMC | 57840 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | CA
75 | Improvement Dst No. 4 | 57895 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | CA
76 | Indian Orchard PV Facility | 57674 | MA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | MA
77 | Jacksonville Solar | 57202 | FL | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
78 | Johnson Matthey, Inc. Solar | 57723 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
79 | Kapaa Photovoltaic Project | 57525 | HI | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
80 | Kent County Wastewater Treatment Solar | 57330 | DE | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | DE
81 | Kingman 1 | 57775 | AZ | IPP Non-CHP | PV, WT | SUN, WND | Multiple | 0 | Yes | 90 |  | AZ
82 | Knouse Solar Project 1 | 57412 | PA | Industrial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
83 | Kohls San Bernardino Solar Facility | 57009 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
84 | L'Oreal Piscataway | 57868 | NJ | Industrial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
85 | La Senita | 57556 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | AZ
86 | Lanai Solar-Electric Plant | 56667 | HI | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
87 | Las Vegas Solar Energy Center | 57576 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NM
88 | Lebanon Solar | 57488 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
89 | Linden Solar Farm | 57381 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
90 | Lockhart Solar PV, LLC | 10444 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 90 | N
91 | Long Island Solar Farm LLC | 57589 | NY | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NY
92 | Longwood Gardens | 57768 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | PA
93 | Los Angeles Harbor College | 57314 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
94 | Los Lunas Solar Energy Center | 57571 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NM
95 | MF Mesa Lane LLC | 56993 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
96 | Macys Goodyear | 57673 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | AZ
97 | Manalapan Village Solar | 57661 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
98 | Maple Solar | 57750 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
99 | Mariani Packing Vacaville Solar | 57005 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 90 | N
100 | Martin | 6043 | FL | Electric Utility | CA, CT, ST | NG, RFO | Multiple | 0 | Yes | 90 |  | FL
101 | Martins Creek Solar NC, LLC | 57461 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NC
102 | Masser Farms Realty Solar | 57494 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | PA
103 | Matrix Buildings A&B (Perth Amboy) Solar | 57384 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
104 | Matrix Stults Road Solar Facility | 57588 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
105 | Mayberry Solar LLC | 57321 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NC
106 | McCormick & Co. Inc. at Belcamp | 57646 | MD | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | MD
107 | McGraw Hill Solar | 57662 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
108 | McKee City Solar Phase 2 | 57863 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 90 |  | NJ
109 | Meridian Vineyards | 57982 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 | Y
110 | Mesquite Solar 1 | 57707 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | AZ
111 | Metro Support Services Center Solar | 57313 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
112 | Mill Creek Solar | 57728 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | NJ
113 | Morgantown Solar Park | 57362 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | PA
114 | Murphy Farm Power, LLC | 57677 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | NC
115 | Murray Hill Solar | 57471 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | NJ
116 | NEDC Solar Site | 57270 | MA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
117 | NJ Oak Solar Plant | 57948 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | NJ
118 | NJMC Landfill | 57724 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | NJ
119 | Napoleon Solar I | 57462 | OH | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | OH
120 | Nellis Air Force Base Solar Array | 56568 | NV | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
121 | Nevada Solar One | 56405 | NV | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 91 | N
122 | Ocotillo | 116 | AZ | Electric Utility | GT, PV, ST | NG, SUN | Multiple | 1 | No | 91 | N
123 | PPL Renewable Energy Merck Solar | 56889 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
124 | PSEG Hackettstown | 57204 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
125 | Pacific Cruise Ship Terminals Berth 93 | 57309 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
126 | Palo Verde College | 57773 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | CA
127 | Paloma Solar Hybrid | 57562 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | AZ
128 | Pennsauken Solar | 56883 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 91 | N
129 | Perdue Bridgeville Photovoltaic | 57772 | DE | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 91 |  | DE
130 | Perdue Salisbury Photovoltaic | 57879 | MD | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 | Y
131 | Pilesgrove | 57448 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | NJ
132 | Pocono Solar Project | 57367 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
133 | Poseidon Solar, LLC | 57318 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | AZ
134 | Prescott Airport | 56228 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
135 | Questa Solar Facility | 57369 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | NM
136 | RE Ajo 1 LLC | 57795 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | AZ
137 | RE Bagdad Solar I LLC | 57790 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | AZ
138 | RMQ 1 and 2 | 56966 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
139 | RP-Orlando, LLC | 57565 | FL | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | FL
140 | RV CSU Power II LLC | 57507 | CO | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
141 | RV CSU Power LLC | 57141 | CO | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
142 | Rancho Seco Solar | 529 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
143 | Rinehart | 57685 | FL | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | FL
144 | Roadrunner Solar | 57338 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | NM
145 | Robert O Schulz Solar Farm | 57579 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
146 | Roger Road WWTP | 57524 | AZ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
147 | Romark PA Solar | 57465 | PA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 92 |  | PA
148 | SAS Solar Farm | 56915 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 92 | N
149 | SEGS III | 10439 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 92 | N
150 | SEGS IV | 10440 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 92 | N
151 | SEGS IX | 10446 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 92 | N
152 | SEGS V | 10441 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 92 | N
153 | SEGS VI | 10442 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 92 | N
154 | SEGS VII | 10443 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 92 | N
155 | SMUD at Fleshman | 57671 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 | Y
156 | SMUD at Grundman | 57669 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 |  | CA
157 | SMUD at Lawrence | 57753 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 |  | CA
158 | SMUD at Van Conett | 57670 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 |  | CA
159 | SPS1 Dollarhide | 57736 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 |  | NM
160 | SPS2 Jal | 57737 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 |  | NM
161 | SPS3 Lea | 57738 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 93 |  | NM
162 | SPS4 Monument | 57739 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 94 | Y
163 | SPS5 Hopi | 57740 | NM | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 94 |  | NM
164 | Sacramento Soleil LLC | 56875 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 94 | N
165 | Saguaro | 118 | AZ | Electric Utility | GT, OT, ST | NG, SUN | Multiple | 1 | No | 94 | N
166 | San Luis Valley Solar Ranch | 57317 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 94 |  | CO
167 | Sand Drag LLC | 57361 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 94 |  | CA
168 | Seabrook Solar Plant | 57667 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 94 |  | NJ
169 | Shelby Solar Energy Generation Facility | 57200 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 94 | N
170 | Sierra SunTower Solar Gen Station | 57323 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 94 | N
171 | Silver Lake Solar Farm | 57341 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 94 | N
172 | Silver Lake Solar Photovoltaic Facility | 57676 | MA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 94 |  | MA
173 | Solar Blythe LLC | 56939 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 94 | N
174 | Solar Park Gainesville, LLC | 57438 | FL | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 | Y
175 | Solar Photovoltaic Project #01 | 56976 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 95 | N
176 | Solar Photovoltaic Project #02 | 56996 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 95 | N
177 | Solar Photovoltaic Project #03 | 57217 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 | N
178 | Solar Photovoltaic Project #06 | 57220 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 | N
179 | Solar Photovoltaic Project #08 | 57222 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 | N
180 | Solar Photovoltaic Project #09 | 57223 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 | N
181 | Solar Photovoltaic Project #22 | 57237 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 | N
182 | Solar Star North Carolina II LLC | 57435 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 |  | NC
183 | Space Coast Next Gen Solar Energy | 56930 | FL | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 95 | N
184 | Springerville | 8223 | AZ | Electric Utility | PV, ST | SUB, SUN | Multiple | 1 | No | 95 | N
185 | Staples La Mirada, CA | 57683 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 |  | CA
186 | State-Fuel Level Increment | 99999 | -- | -- | -- | -- | -- | 1 | No | 95 | N
187 | Stockton Athletic Center | 57864 | NJ | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 95 |  | NJ
188 | Stroud Solar Station | 57497 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 96 | Y
189 | Summit Associates | 57726 | NJ | Electric Utility | -- | -- | -- | 0 | Yes | 96 |  | NJ
190 | Sun City Project LLC | 57360 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 96 |  | CA
191 | Sun Farmer I | 57445 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
192 | SunE Alamosa | 56481 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
193 | SunEdison Anheuser Busch Fairfield | 57010 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
194 | SunEdison Ironwood State Prison | 57007 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
195 | SunEdison LV Sutton Plant Site | 56938 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
196 | SunEdison Procter & Gamble Oxnard | 57008 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
197 | SunEdison Walgreens Moreno Valley | 57004 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
198 | SunEdison Walmart Apple Valley DC | 57012 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
199 | Sunray 2 | 10437 | CA | IPP Non-CHP | CP | SUN | Solar Thermal with Energy Storage | 1 | No | 96 | N
200 | Sunray 3 | 10438 | CA | IPP Non-CHP | ST | SUN | Solar Thermal without Energy Storage | 1 | No | 96 | N
201 | Sunset Reservoir North Basin | 57559 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
202 | Taylorsville Solar LLC | 57402 | NC | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 96 | N
203 | Temescal Canyon RV, LLC | 57656 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 96 |  | CA
204 | The City of Vineland at North Vineland | 57746 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 96 |  | NJ
205 | The City of Vineland at West Vineland | 57745 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 97 | Y
206 | Titusville Solar | 57815 | NJ | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 97 |  | NJ
207 | Toys R Us- DE, Inc. at Mt. Olive, NJ | 57647 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 97 |  | NJ
208 | Trenton Solar Farm | 57352 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 97 | N
209 | Trexlertown Solar Array North and South | 57519 | PA | Industrial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 97 |  | PA
210 | UASTP I | 57392 | AZ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 97 | N
211 | Univ of California San Diego Solar | 57856 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 97 |  | CA
212 | Vaca Dixon Solar Station | 57041 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 97 | N
213 | Victor Valley CC CPV Solar | 57254 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 97 | N
214 | Vineland Headquarters | 57742 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 97 |  | NJ
215 | Vineland Mays Landing Solar | 57660 | NJ | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 98 | Y
216 | WEA Texas Bayonne | 57383 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 98 | N
217 | WWRF Solar Plant | 56922 | CO | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 98 | N
218 | Walgreens Woodland Distribution Center | 57006 | CA | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 98 | N
219 | Walmart Casa Grande | 57939 | AZ | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 98 |  | AZ
220 | Webberville Solar Project | 57699 | TX | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 99 | Y
221 | Western 102 Power Plant | 56500 | NV | Industrial Non-CHP | IC, PV | NG, SUN | Multiple | 1 | No | 99 | N
222 | Westside Solar Station | 57499 | CA | Electric Utility | PV | SUN | Solar Photovoltaic | 0 | Yes | 100 | Y
223 | Wild Horse | 56322 | WA | Electric Utility | PV, WT | SUN, WND | Multiple | 1 | No | 100 | N
224 | William Paterson University | 57805 | NJ | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 100 |  | NJ
225 | Wyandot Solar Farm | 57203 | OH | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 100 | N
226 | Yamhill Solar LLC | 57652 | OR | IPP Non-CHP | PV | SUN | Solar Photovoltaic | 0 | Yes | 100 |  | OR
227 | Yankee Street | 2854 | OH | Electric Utility | GT, PV | NG, SUN | Multiple | 0 | Yes | 100 |  | OH
228 | Yardville Solar Farm | 57382 | NJ | Electric Utility | PV | SUN | Solar Photovoltaic | 1 | No | 100 | N
229 | Yolo County Solar Project | 57422 | CA | Commercial Non-CHP | PV | SUN | Solar Photovoltaic | 1 | No | 100 | N

## Exclusions
Exclusions
[8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
EIA | Name | State | FirstYr | MWp | Yr1 p50 MWh | Reason to exclude |  | 1: Output
12137/141 | Agua Fria PV-3 | AZ | 2003 | 0.2576 | 574.7056 |  |  | 395 | 297 | 111 | 285 | 398 | 437 | 201 | 438 | 447 | 437 | 395 | 255 | 0 | 153 | 217 | 281 | 136 | 0 | 0 | 0 | 0 | 21 | 79
[5 empty] | PI stdev&avg | 0.29358 | 0.37698 | 0.68731 | 0.51679 | 0.19314 | 0.49591 | 0.69253 | 0.76039 | 0.34974 | 0.76213 | 0.77779 | 0.76039 | 0.68731 | 0.44371 | 1.74e-06 | 0.26622 | 0.37758 | 0.48895 | 0.23664 | 1.74e-06 | 1.74e-06 | 1.74e-06 | 1.74e-06 | 0.03654 | 0.13746
[5 empty] | rank |  |  | 26.09% | 34.78% | 69.57% | 39.13% | 21.74% | 13.04% | 56.52% | 8.696% | 4.348% | 13.04% | 26.09% | 47.83% | 82.61% | 60.87% | 52.17% | 43.48% | 65.22% | 82.61% | 82.61% | 82.61% | 82.61% | 78.26% | 73.91%
[5 empty] | p(XX) |  |  | 1: 1.057
[8 empty] | 0.14525 | 0.31696 | 0.7344 | 0.34271 | 0.14123 | 0.095781 | 0.53696 | 0.094777 | 0.086088 | 0.095781 | 0.14525 | 0.4101 | 0.90044 | 0.64701 | 0.49918 | 0.35146 | 0.68368 | 0.90044 | 0.90044 | 0.90044 | 0.90044 | 0.8769 | 0.79271
10444 | Lockhart | CA | 2005 |  |  | PV didn't go in until 2023
116 | Ocotillo | AZ | 2005 |  |  | PV dropped 95% after two years, ran for 10, died by 2016, first year 2005
56228 | Prescott | AZ | 2005 |  |  | Changed capacity many times; the records are a mess
529 | Rancho Seco | CA | 2005 |  |  | Died off at 10 years into EIA records, dead by 2012
10439 | SEGS III | CA | 2005 |  |  | thermal
10440 | SEGS IV | CA | 2005 |  |  | thermal
10446 | SEGS IX | CA | 2005 |  |  | thermal
10441 | SEGS V | CA | 2005 |  |  | thermal
10442 | SEGS VI | CA | 2005 |  |  | thermal
10443 | SEGS VII | CA | 2005 |  |  | thermal
118 | Saguaro | AZ | 2005 |  |  | mislabeled; there is no solar
8223 | Springerville | AZ | 2005 |  |  | Changed capacity all the time
10437 | Sunray 2 | CA | 2005 |  |  | PV started 2017
10438 | Sunray 3 | CA | 2005 |  |  | PV started 2017
56574 | MMA RC Power | CA | 2007 |  |  | Fucking burned up POS worked for barely one year - Long Beach Conv Center rooftop
56405 | Nevada Solar One | NV | 2007 |  |  | Thermal
56861 | MMA Belmar | CO | 2009 |  |  | Stopped reporting after 3 years; Brad Eccles did IE on this 1.74 MWp/1.68 MW fixed 10-deg parking structure canopy Sunpower 210 modules
56814 | ELACC MMA | CA | 2008 |  |  | Stopped reporting after 9 years
56909 | Gap | CA | 2009 |  |  | Steady for 10 years, then a tripling in output in output by 2021, and a steady decline since. So system has dramatically been changed in size.
56966 | RMQ1&2 | NC | 2008 |  |  | System got a lot bigger yr9, then faded partway wacko down four years later. It's just too weird to follow, obviously not a consistent size or operation
56943 | Ausra | CA | 2009 |  |  | Only ran 5 yrs and erratically at that
57140 | Maricopa | AZ | 2010 |  |  | Only ran one year. Nonsense data point.
56976 | Solar PV #01 | CA | 2009 |  |  | Ran 3 years
57694 | NREL Main | CO | 2011 |  |  | Ran 9 years and seems to have gotten larger
57692 | NREL NWTC Bldg | CO | 2011 |  |  | Ran 7 of 9 years, piece of shit
57506 | FRV SI Transport | CA | 2010 |  |  | Ran 6 yrs, zero for a year, then two inexplicable 50% higher years, then revert to its earlier trend. Too unexplained and weird to include, and only shows 11 sensible years out of 15. Piece of shit.
57323 | Sierra Suntower | CA | 2010 |  |  | Thermal
57445 | Sun Farmer | NC | 2010 |  |  | Stillbirth - nothing in any year!?
57254 | Victor Valley | CA | 2010 |  |  | CPV
57372 | Bellevue Solar Project | OR | 2011 |  |  | Too short, 9 yrs, died 2021
57747 | FedEx Field Solar Facility | MD | 2012 |  |  | Huge bogus jump in 2022, then died after 11 yrs operation
57591 | Hatch Solar Energy Center I, LLC | NM | 2012 |  |  | Showed second half 50% increase - nonsense unless size is changing
these two were removed and replaced with PI equivalents in order to introduce two new states into the national mix
57640 | 500 Virginia | PA | 2012 | 2011 | IPP Non-CHP | Fixed | 10 |  | 40.139 | -75.192 | 1 | 1 | 1552.3125 | Philadelphia | 12.4 | 35.3867 |  | 1241.85 | 1227 | 0 | 1129 | 1103 | 1238 | 1174 | 1108 | 1029 | 1070 | 1303 | 467 | 1285 | 1132
57574 | ETS Ewing | NJ | 2014 | 2010 | IPP Non-CHP | Fixed | 5 |  | 40.2818 | -74.794 | 1.4 | 1.3 | 1497.525 | Philadelphia | 12.4 | 34.9795 |  | 1677.228 | 2052 | 2121 | 2109 | 1992 | 1815 | 2237 | 1609 | 1543 | 1237 | 809 | 1011
61497 | Elbe Solar Center | OR | 2018 |  |  | No data for 2024, so period is too short

## NullOverlap
7-year PI probability overlaps for Old 100 and New 25 systems |  |  |  | Old 100 | New 25 | Old 100 | New 25
|  |  |  | 1-sided | 1-sided
Set | PI7 | Stdev | PI | Cumul Prob | Cumul Prob | Density | Density
Old 100 | 0.92 | 0.11 | 0.1 | 4.5089e-14 | 6.1255e-10 | 3.1088e-12 | 2.9372e-08
New 25 | 0.89 | 0.13 | 0.3 | 8.6839e-09 | 2.8333e-06 | 4.582e-07 | 0.00010334
|  |  | 0.5 | 6.7219e-05 | 0.0013499 | 0.0024765 | 0.034091
Question: is the new distribution different from |  |  | 0.7 | 0.02275 | 0.071934 | 0.49083 | 1.0547
the old one? |  |  | 0.75 | 0.061118 | 0.14076 | 1.0987 | 1.7184
Answer: we use the null hypothesis, assuming they |  |  | 0.8 | 0.13766 | 0.24437 | 2.0003 | 2.4149
are the same number, then calculate the probability |  |  | 0.85 | 0.26227 | 0.37916 | 2.962 | 2.9269
that the two numbers are the same. |  |  | 0.9 | 0.42786 | 0.53066 | 3.5673 | 3.0597
|  |  | 0.95 | 0.60747 | 0.67779 | 3.4943 | 2.7587
Assume reference distribution is the old one |  |  | 1 | 0.76647 | 0.80127 | 2.784 | 2.1453
The delta Z is: |  |  | 1.05 | 0.88136 | 0.8908 | 1.804 | 1.4389
-0.27273 |  |  | 1.1 | 0.94912 | 0.94689 | 0.95075 | 0.83239
At this value of Z, the cumul area under the ref curve: |  |  | 1.3 | 0.99972 | 0.99919 | 0.009292 | 0.021235
0.39253 |  |  | 1.5 | 1 | 1 | 3.3302e-06 | 5.0801e-05
The probability that these are the same value, that is, the null hypothesis, looks
|  |  | Iterate to find the PI with equal probability: |  |  |  |  | at the % overlapping area beneath the two curves
|  |  | 0.8456 | 0.2494 | 0.36635 | 2.8852 | 2.8949 | Here, the area common to both distributions is pretty high, so they don't appear to
|  |  | To the right of this crossover PI value, the ref curve holds |  |  |  |  | be very different, at least not at a high confidence
|  |  | 75.06% | of its area
To the right of this crossover PI value, the newer test curve holds
63.37%
So the area common to both curves must be the sum of the gray
|  |  | portion to the left of the crossover, or |  |  | 24.94%
plus the area beneath the gold curve to the right of the crossover:
63.37%
The total area common to both curves is:
88.31%
So the chance that these are different distributions is small, just
11.69%